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1.0 Introductory Matters and Background

1.1 Client:


Text based




Excel 
	Blocks:
	 



	School 
	 

	Building Condition Report
	

	Block One:
	

	Reception, Administration, Main Hall, Refrectory/Kitchen, Sixth form centre the associated linking corridors, stairs etc.
	

	ELEMENT
	Element No.
	Description of Construction
	Description of Condition
	Condition Rating
In accord with provided rating system.
	Risk Rating
	Suggested Remedial Repair/Investigation
	Costings
	Alternative Recommended Option
	Comments

	Roof
	1
	 
	 
	Condition Rating
	Priority
	Weighting
	 
	 
	 
	 
	 

	Roof structure
	1.1
	Woodwool slab with felt coverings
	Visible only in limited areas of the Hall, stores etc.
	D
	1
	 
	 
	Health and Safety Issue. Deleterious material.
	 
	 
	 

	Coverings (incl. glazed roof lights)
	1.2
	Broken and cracked roof-lights are contributing to water penetration internally that is damaging the interior finishes. Green mineral finished felt roof coverings.
	Not seen due to access. Assume that it is in similar condition generally to the felt to that of the library. Water penetration arising.
	D
	1
	 
	 
	 
	 
	 
	 

	Insulation Drainage (including rainwater goods and pipes)
	1.3
	Assumed that some PIR Insulation added when last recovered as per the Library roof. The felt is likely to be aged.
	 
	D
	1
	 
	 
	 
	 
	 
	 

	Parapets,
	1.4
	Not Applicable.
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Handrails etc.
	1.5
	There are no handrails apparent.
	Consider maintenance access.
	D
	1
	 
	 
	Hand-rail or a fall arrest system should be added to aid maintenance repairs.
	 
	 
	 

	Frame Other (including chimneys)
	1.6
	Extract ventilation from Kitchen
	Service and clean.
	B-C
	1
	 
	 
	 
	 
	 
	 

	Boiler Flues and Extract
	1.7
	Not applicable.
	 
	 
	 
	 
	 
	 
	 
	 
	 

	Eaves (Fascia/Soffit/Barge).
	1.8
	These were originally of timber with asbestos boarded soffits. In many areas the timber fascia has since been over-clad with now badly deteriorated paint coated galvanised steel sheets or PVC boards.
	Peeling paint, concealed asbestos containing materials and deteriorating timber work, especially at exposed corners where wind eddies arise.
	D
	1
	 
	 
	 
	 
	 
	 

	Rainwater gutters and downpipes
	1.9
	Aluminium gutters and cast aluminium and cast-iron rainwater downpipes.
	Many gutters are now blocked or leaking. Down-pipes are damaged or missing.
	D
	 
	 
	 
	 
	 
	 
	 

	Tank Room
	1.1
	Colour-coated trapezoidal steel wall cladding 
	Water leaks?
	C
	 
	 
	 
	Reclad as part of refit.
	 
	 
	 

	Building Structure
	2
	 
	 
	 
	 
	 
	 
	 
	 
	 
	 















Powerpoint/Word/ Paint etc.


[bookmark: _GoBack]Defective asbestos sheet roof coverings. There is also debris that has fallen from above, or been thrown by vandals onto the roof.
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Safe maintenance access to these areas was always almost impossible.
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