1.a.

Notes:

1a. 	Cos(25) = 0.9063

| Correction Capacitor | None | C2 – 10uF | C2 + C3 – 20uF | C2 + C4 – 15uF |
| --- | --- | --- | --- | --- |
| Phase Angle (Lead/Lag) | 24° Lag | 4° Lag | 10° Lead | 8° Lead |
| Current Amplitude | 650mA | 536mA | 520mA | 606mA |

1b. 	C2 – 10uF gives the nearest to complete correction of the phase angle.

1c. 	Using the best capacitor value of power factor correction in the circuit the best description of it out of a, b, c, d is C. Phase angle is a minimum and current a maximum.

1d. 	Cos(24) = 0.913

1e. 	Cos(4) = 0.913

2.486 x 2 x 10 = 49.72V

1f. 	49.72 x 650x10-3 x cos(24) = 29.52	therefore	29.52/8 = 3.69W

1g.	49.72 x 536x10-3 x cos(4) = 26.59	therefore	26.59/8 = 3.32W

Power factor correction is normally achieved by using extra capacitors to compensate for the reactive power demand. In this case, it is clear to see that by using the best correction capacitor in the circuit, the overall power usage has decreased. This in real life terms would mean a reduction of power consumption therefore lower electricity bills and also extended equipment lifetimes.

Notes:

The fault code entered was fault 9.

| Correction Capacitor | None | C2 – 10uF | C2 + C3 – 20uF | C2 + C4 – 15uF |
| --- | --- | --- | --- | --- |
| Phase Angle (Lead/Lag) | 44° Lag | 22° Lead | 50° Lead | 45° Lead |
| Current Amplitude | 314.2mA | 262.8mA | 480mA | 360mA |

Initially there was a higher inductance measured as the phase angle lagged further and the current was lower. It is proposed that C1 is now open circuit, if this is the case the current would flow through winding 2 & 3 as shown in the image below.

This was tested by removing the link shown in the image to the right. Once this was removed the motor stopped functioning.