Module:

Material science and building services (ACBA 4006)

Assignment title: Lighting layout and sound index calculation

Prepared for:

Allan Nantel

Created by:

Jake Roberts

Contents 										Page

- Introduction									 2

- Task A the required lighting for the factory				 2-5

- Drawing layout for the laps of the factory					 5

- Task B the sound reduction index 					 6-7

- The implications and factors of frequency and wavelength it sound.	 7

- Introduction

The aim of this assignment is to 1st calculate the number of lamps required in a factory and provide a design for the luminaire installation. This can only be done by first identifying the room index, utilisation factor and the suitable layout for the lamp fittings, including a suitable drawing for the layout of the lamps. 2nd part of the assignment is to calculate the sound reduction efficiency through the external wall including the window efficiency

- Task A

Calculate the Room index, utilisation factor, the number of lamps required and a suitable layout for the lamp fittings (Value of s). for a production area in a factory that is 60 metres x 24 metres x 8 metres in height. The factory benches are a height of 1 metre above the floor level. The area reflectance’s are 0.3 for the ceiling and 0.5 for the walls the lighting design specifies fluorescent lamps in recessed louvre with DLOR of 50%. With a lighting design lumen output of 18,000 lumens. The illumination required for the factory area is 200 lux at the working plane light loss factor= 0.75.

Room Index

To calculate the Room Index, the following formula is used;

RI = 	 (L x W)

(Hm (L + W))

Where;

RI = Room Index

L = Length of room (60 mtr)

W = Width of room (24 mtr)

Hm = Height of the luminaire measured from the working plane (8-1 = 7 mtr)

Therefore;

RI = (60 x 24)

(7 (60 + 24))

RI= (1440)

7 x 84

RI= 1440

588

RI = 2.45

Utilisation Factor

Using the utilisation factor table hand out (a cropped version is shown below), the utilisation factor equals 0.46. This is because the ceilings reflectance is 0.3 and the walls reflectance is equal to 0.5, with a room index of 2.45.

|  |  |  | Reflectance’s |  |  |
| --- | --- | --- | --- | --- | --- |
| Description of fitting | Basic downward LOR% | Ceiling | 0.3 |  |  |
|  |  | Walls | 0.5 | 0.3 | 0.1 |
|  |  | Room Index |  |  |  |
| Recessed louvre 0.23 trough with optically designed reflecting surfaces |  | 0.8 | 0.33 | 0.30 | 0.28 |
|  |  | 1.0 | 0.37 | 0.34 | 0.32 |
|  |  | 1.25 | 0.40 | 0.37 | 0.35 |
|  |  | 1.5 | 0.42 | 0.39 | 0.38 |
|  |  | 2.0 | 0.44 | 0.42 | 0.41 |
|  |  | 2.5 | 0.46 | 0.44 | 0.43 |
|  |  | 3.0 | 0.47 | 0.45 | 0.44 |

Number of lamps required

As I calculated the room index and utilisation factor, I could now find the number of lamps required in the factory. This was done by using the formula below;

N= E x A

F x UF x LLF

Where;

N = Number of lamps required

E= Illuminance level required (200 lux)

A= Area at working plane height (60 x 24 = 1400 m²)

F= Average luminous flux from each lamp (18000 lumens)

UF= Utilisation factor, an allowance for the light distribution of the luminance and the room surfaces (0.46)

LLF= Light loss factor, an allowance for a reduction in light output caused by lamp deterioration and dirt (0.75)

Therefore;

N=    200 x 1400

18000 x 0.46 x 0.75

N=    288000

6210

N= 46.38

Therefore 47 lamps

Suitable layout for the lamp fittings

As the factory requires fluorescent lamps, the total spacing (SMAX) would equate to 10.50m apart, as shown below.

SMAX = 1.5 x Hm

SMAX = 1.5 x 7

SMAX = 10.50m apart

3.0 Drawing layout for the required laps of for the factory

4.0 Task B

calculate the sound reduction index for a wall 20m2 that contains an area of 4m2, the values of the sound reduction indexes are: 50dB for the brickwork and 10dB for the window area.

Brick = T1 =? A1 = 20-4 = 16m2 SRI = 50dB

Window = T2 =? A2 = 20-16 = 4m2 SRI = 10dB

Using the SRI formula SRI = 10x(log10(1/T))

T0 = (T1xA1) + (T2xA2)/A1+A2

Brick wall = 50 = 10(log10(1/T1))

5 = log10(1/T1)

1/T1 = 10-5

T1 = 10-5

Window = 10 = 10(log10(1/T2))

1 = log10(1/T2)

1/T2 = 10-1

T2 = 10-1

= (10-5 x 16) + (10-1 x 4)/16+4

= 0.40016/20

= 0.02008

= 0.02008

Using SRI formula and substituting

SRI = 10x(log10(1/T))

= 10 x (log10(1/0.02008))

= 10 x (log10(49.8007))

= 16.97235447

= 17dB

SRI for the Composite partition = 17dB

5.0 The implications and factors of frequency and wavelength it sound.

There are two main types of sound, these are infrasound which is low frequency and ultrasound which is a high frequency. The average sound range for a human is anywhere between 20 & 20,000 HZ. infrasound is below 20 HZ which is regarded as a low frequency. Ultrasound is anything over the 20,000 HZ which is classified as high frequency.

We generally measure the wavelengths and frequency of sound and the way it travels. This is measured to control the output of not only speakers for concerts and other events but also to help protect or silent the ultrasound frequencies to prevent nuisance for human beings and the environment such places would be dwelling airports e.c.t. the way in which sound is monitored is through Decibels this is normally calculated by the pascals in which can be monitored by human hearing.