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[bookmark: _Toc133317136]1.0 Abstract

This concise written report research variable frequency drives and the resulting harmonics caused by the use of them. The information is then used to design and specify suitable technologies to control different motor systems.
The software Proteus will be used to carryout practical demonstrations to compare and contrast how different components can be used to minimise the effects of harmonics on the supply by rectifying the incoming mains.  

Word Count: 3009 (tables do not count towards the overall word count)
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A factory is to refit its motor drive systems. There are five types of induction motor in the factory as shown in the table below:
	
	Motor A
	Motor B
	Motor C
	Motor D
	Motor E

	Power
	500KW
	80KW
	10KW
	5KW
	1KW

	Phases
	3
	3
	3
	3
	1

	Voltage
	400
	400
	400
	400
	230

	Required to be Reversible ?
	Yes
	Yes
	Yes
	No
	No

	Variable Speed Required ?
	Yes
	Yes
	Yes
	No
	No

	Quantity Installed
	5
	10
	23
	17
	127

	Example Application
	Rolling Mill
	Gantry Crane
	Conveyor
	Cutting Machine
	Pumps / Fans

	
	2500kW
	800kW
	230kW
	85kW
	127kW


[bookmark: _Toc133317128]Table 1 - Motor Specifications
Specify a suitable technology for the motor drive system. You should consider things like the use of a common DC Bus, starters, protection, cost, flexibility of control system, information gathering ability, etc.



[bookmark: _Toc133317138]2.1 Research Variable Frequency Drives

‘’A variable frequency drive (VFD) is a type of motor controller that drives an electric motor by varying the frequency and voltage of its power supply. The VFD also has the capacity to control ramp-up and ramp-down of the motor during start or stop, respectively.
Even though the drive controls the frequency and voltage of power supplied to the motor, we often refer to this as speed control, since the result is an adjustment of motor speed.
There are many reasons why we may want to adjust this motor speed. 
For example, to
· Save energy and improve system efficiency
· Convert power in hybridization applications
· Match the speed of the drive to the process requirements
· Match the torque or power of a drive to the process requirements Improve the working environment.
· Lower noise levels, for example from fans and pumps
· Reduce mechanical stress on machines to extend their lifetime Shave peak consumption to avoid peak-demand prices and reduce the motor size required

In addition, today’s drives integrate networking and diagnostic capabilities to better control performance and increase productivity. So, energy savings, intelligent motor control and reduction of peak-current drawn are three great reasons to choose a VFD as the controller in every motor-driven system.
The most common uses of a VFD are for control of fans, pumps and compressors, and these applications account for 75% of all drives operating globally’’.[1]
[bookmark: _Toc101732197]



Figure 1 shows the block diagram for a variable frequency drive in its most basic form where it is supplied by a three phase supply. This AC supply then gets converted to DC onto the DC bus, where the next stage is the for the converter to create an output frequency using pulse width modulation so that the speed of the motor can be controlled. 

[image: ]
[bookmark: _Toc133317105]Figure 1 - Block Diagram of VFD
[6]







[bookmark: _Toc133317139]2.1.1 Description of the components of the VFD

	Component
	Description

	Invertor Units
	The inverter unit has capacitors built in to smooth the voltage of the DC busbars. The connections to the common busbars are fused, and the individual INU’s can be disconnected form the busbars via a switch, or a fused isolator.

	IGBT
	The ISU is used when the system is a regenerative one, and its purpose is to convert the three-phase AC supply voltage into a DC voltage. With the use of IBGT’s it means the motors can be operated in both motoring and generating modes.

	Regen Rectifier Unit
	The RRU is used when the system is a regenerative one, and its purpose is the convert the three-phase AC voltage into DC voltage. It is built up of IGBT’s which are switched once during each voltage cycle, which reduces switching losses and allows for a higher power.

	Brake Unit
	The brake unit is what takes care of the generated energy when the motor is decelerating. When the voltage in the circuit rises above a certain point, the breaking chopper brings the braking resistor into circuit.

	DC – DC Converter
	The DC-DC converter allows for the transfer of energy form the DC link, to an external storage, usually in the form of batteries or super capacitors.


[bookmark: _Toc133317129]Table 2 - VFD Components
[1]

[bookmark: _Toc101732203]

[bookmark: _Toc133317140]2.1.2 Speed control

Variable frequency drives increase or decrease the speed of a motor by altering the frequency supplied to the motor. The technique these drives use is called pulse width modulation.
A pulse width modulation inverter works by varying the frequency and pulse widths of the supplied voltage to the induction motor. This is done by switching in and out the Insulated-gate bipolar transistors (IGBT) in the inverter. Below are two different examples of PWM signals that would be supplied to a motor. [2]

[image: ]
[bookmark: _Toc133317106]Figure 2 - Pulse Width Modulation
[2]


[bookmark: _Toc101732204]
[bookmark: _Toc133317141]2.1.3 Dynamic braking

When the input bridge isn’t an active input bridge, power will have to be dissipated using dynamic braking resistors. When the motor slows down, the power will flow back to the inverter from the motor. Due to the input bridge being made up of diodes which are only single direction, the energy from the motor will not be able to flow back into the grid. This means all the power is stuck in the DC link, meaning an overvoltage trip will occur. The addition of a dynamic braking resistor and switch that’s usually a transistor means the energy can be dissipated. Once the voltage in the DC link rises above a certain level the switch will allow the voltage to be dissipated across the resistor. [2]
[image: ]
[bookmark: _Toc133317107]Figure 3 - Dynamic Braking Resistor
[2]



[bookmark: _Toc101732205][bookmark: _Toc133317142]2.1.4 Active front end

An active input bridge or active front end removes the need for dynamic braking resistor circuit. Instead of using single direction diodes, it uses IGBT’s as they are bi directional. This will allow all the generated power from the slowdown to be fed back into the grid to dissipate the energy. When the voltage in the DC link rises to a certain level the transistors will switch allowing the energy created to flow In the reverse direction. [2]
[image: ]
[bookmark: _Toc133317108]Figure 4 - Active Front End
[2]
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[bookmark: _Toc133317144]2.2.1 Motor A - Rolling Mill
	
	ABB VFD Drive
	Schneider VFD Drive
	VYBO VFD Drive
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	Type
	ACS 880-07 Cabinet single drives
	ATV61Q
	V810

	Voltage
	380 to 415V
	380...480 V - 15...10 %
	400V AC ± 15%

	Power
	45 to 2800 kW
	500kW
	500kW

	Variable Speed
	Yes
	Yes
	Yes

	Protection
	• Safe torque off (STO) 
• Safe stop 1 (SS1-t and SS1-r) 
• Safe stop emergency (SSE) 
• Safe brake control (SBC) 
• Safely-limited speed (SLS) 
• Safe maximum speed (SMS) 
• Prevention of unexpected startup (POUS) 
• Safe direction (SDI) 
• Safe speed monitor (SSM) 
• Safe motor temperature (SMT)
	Against exceeding limit speed: drive
Against input phase loss: drive 
Break on the control circuit: drive 
Input phase breaks: drive 
Line supply overvoltage: drive 
Line supply undervoltage: drive 
Overcurrent between output phases and earth: drive 
Overheating protection: drive 
Overvoltages on the DC bus: drive 
Power removal: drive Short-circuit between motor phases: drive 
Thermal protection: drive Motor phase break: motor 
Power removal: motor 
Thermal protection: motor
	Motor short-circuit detection
output phase loss protection
overcurrent protection
overvoltage protection
live protection
overheat protection
overload protection

	Reversable Motor Direction
	Yes
	Yes
	Yes

	Operating Temperature
	0°C to 50°C
	5…55 °C
	– 10 ° C ~ 40 ° C (reduce power level if ambient temperature is between 40 ° C to 50 ° C)

	Degree of Protection
	IP22 Standard
IP42 & IP54 Options
	IP00 conforming to EN/IEC 60529 
IP00 conforming to EN/IEC 61800-5-1 
IP30 on side parts conforming to EN/IEC 60529 
IP30 on side parts conforming to EN/IEC 61800-5-1 
IP30 on the front panel conforming to EN/IEC 60529 
IP30 on the front panel conforming to EN/IEC 61800-5-1 
IP41 on upper part conforming to EN/IEC 60529 
IP41 on upper part conforming to EN/IEC 61800-5-1
	IP22

	Connectivity
	- 2 Analogue inputs
- 2 Analogue outputs
- 6 Digital inputs
- 3 Relay outputs
- Safe Torque off
- Drive to Drive link (EIA 485)
- Built in Modbus
- Assistant control panel (RJ45)
- Bluetooth
	Communication card for APOGEE FLN
Communication card for BACnet 
Communication card for CC-Link 
Communication card for DeviceNet 
Communication card for EtherNet/IP 
Communication card for Fipio 
Communication card for Interbus-S 
Communication card for LonWorks 
Communication card for METASYS N2 
Communication card for Modbus Plus 
Communication card for Modbus TCP 
Communication card for Modbus/Uni-Telway 
Communication card for Profibus DP 
Communication card for Profibus DP V1 
Controller inside programmable card 
I/O extension card
	8 digital inputs
binary ON / OFF inputs
1 terminal X5 can support high speed pulse input
All terminals have optional PNP or NPN
2 analog inputs
one of which FIV supports -10 V / +10 V; or a 0-10 V input and the second FIC supports a 0-10V or 0-20mA (4-20 mA) input.
1 Programmable open collector output: provides 1 output terminal (open collector output or high speed pulse output)

2 relay outputs

2 analog outputs: FOV and FOC with optional 0 – 20 mA (4 – 20 mA) or 0 – 10 V output


	Price
	
	
	


[bookmark: _Toc133317130]Table 3 - Rolling Mill System

The control system selected for the five rolling mill motors are the ABB ACS 880-07 which are cabinet single drives with each having their own 400V supply. Figure 5  shows that they will be R11 frame size code ACS880-07-0880A-5+C129.
As the e room where these will be housed is not restricted in space the control system will consist of six of these drives five will control five different motors which will need to have their own VFD’s due to running at different speeds for the rolling mill. The sixth drive will be a standby drive which can be switched in to run any of the motors in the case of any one of the drives going down or for carrying out maintenance on the other drives without taking the mill offline.

[image: ]
[bookmark: _Toc133317109]Figure 5 - ACS880-07 Specifications
[3]





[bookmark: _Toc133317145]2.2.2 Motor B - Gantry Crane
	
	Vacon VFD Drive
	ABB VFD Drive
	Allen Bradley VFD Drive
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	Type
	NXP 0168
	ACS880 Multidrive
	Power Flex 750-Series 20F1ANC205

	Voltage
	380 -500V
	380 to 415V
	380 – 400V

	Power
	90kW
	1.5 to 6000kW
	0.37 – 200kW

	Variable Speed
	Yes
	Yes
	Yes

	Protection
	Overvoltage 
undervoltage 
earth fault 
mains supervision 
motor phase supervision 
overcurrent 
unit overtemperature 
motor overload 
motor stall 
motor underload
short-circuit of +24 V and +10 V reference voltages
	• Safe torque off (STO) 
• Safe stop 1 (SS1-t and SS1-r) 
• Safe stop emergency (SSE) 
• Safe brake control (SBC) 
• Safely-limited speed (SLS) 
• Safe maximum speed (SMS) 
• Prevention of unexpected startup (POUS) 
• Safe direction (SDI) 
• Safe speed monitor (SSM) 
• Safe motor temperature (SMT)
	[bookmark: _GoBack]AC input overvoltage trip 
AC input undervoltage trip 
Bus overvoltage trip 
Bus undervoltage shutoff 
Nominal bus voltage (full load) 
Drive overcurrent trip Software overcurrent trip Instantaneous current limit Hardware overcurrent trip 
Line transients 
Control logic noise immunity 
Power ride-through 
Logic control ride-through 
Ground fault trip 
Short circuit trip


	Reversable Motor Direction
	Yes
	Yes
	Yes

	Operating Temperature
	Maximum operating temperature of +35°C
	0°C to 50°C
	0 to 50°C

	Degree of Protection
	IP54
	- IP22 Standard
- IP42 & IP 54 Options
	IP54

	Connectivity
	RS485 with screw terminal RS485 with screw terminal  
PROFIBUS DP with screw terminal OPTE5 
PROFIBUS DP with D9-connector 
OPTE6 CANopen CANopen 
OPTE7 DeviceNet DeviceNet 
OPTE8 RS485 with D9-connector 
RS485 with D9-connector 
OPTE9 Dual-port Ethernet Dual-port Ethernet 
OPTEA Advanced Dual-port Ethernet Advanced Dual-port Ethernet 
OPTC2 RS485 with screw terminal 
RS485 with screw terminal 
OPTC3 PROFIBUS DP with screw terminal 
OPTC4 LonWorks
OPTC5 PROFIBUS DP with D9-connector 
PROFIBUS DP with D9-connector 
OPTC6 CANopen CANopen 
OPTC7 DeviceNet DeviceNet 
OPTC8 RS485 with D9-connector 
RS485 with D9-connector
	- 2 Analogue inputs
- 2 Analogue outputs
- 6 Digital inputs
- 3 Relay outputs
- Safe Torque off
- Drive to Drive link (EIA 485)
- Built in Modbus
- Assistant control panel (RJ45)
- Bluetooth
	BACnet/IP option module 
Coaxial ControlNet option module 
ControlNet communication adapter (coax) 
DeviceNet option module 
DeviceNet communication adapter 
Dual-port EtherNet/IP option module 
EtherNet/IP communication adapter 
CANopen communication adapter  
LonWorks communication adapter  
Modbus/TCP communication adapter 
Profinet I/O option module 
Dual-port Profinet I/O option module 
PROFIBUS DP communication adapter 
ControlNet communication adapter
Remote I/O communication adapter 
RS-485 DF1 communication adapter 
External communication kit power supply


	Price
	
	
	


[bookmark: _Toc133317131]Table 4 - Gantry Crane System
 
For the control system on the gantry crane the ABB VFD ACS880 multidrive system has been selected. The reason being the 10 motors being supplied from one 400V supply creating a common DC bus. This will be beneficial because the drive system will have to be installed on the crane where space is limited. Using the specification table in figure 6 the drive type to be installed in the multidrive housing will be the ACS880-107-025OA-3 frame size R6i. The drive is rated at 90kW which is slightly higher than the 80kW required. The reason for choosing this module is that due to the crane being classed as M8. This is the highest duty meaning the crane is a production crane and in service for 24 hours a day. So it is because of this the heavy duty section was used and the one below this model is only rated at 75kW. 

[image: ]
[bookmark: _Toc133317110]Figure 6 - ACS880-107 Specifications
[3]

[bookmark: _Toc101732196]

[bookmark: _Toc133317146]Difference between single and multidrive systems

Single drives have a three phase input usually 415V 50Hz supply and produces a variable voltage but more importantly a variable frequency to the motor. This controls the speed and the torque of the motor.
[image: ]
[bookmark: _Toc133317111]Figure 7 - Illustration of Single Drive
[2]
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[bookmark: _Toc133317112]Figure 8 - Circuit Layout of Single Drive
[2]

Multidrives can control the speed and torque of multiple AC motors individually. A three phase supply is applied to the input bridge, which rectifies the AC supply to produce a common DC Bus. The multidrive then has an inverter module for every motor that uses the DC Bus supply to create variable frequency and variable voltage to control the individual motors.
The crane’s multidrive system means there is a common DC bus arrangement, enabling single power entry and common braking resources for several drives. There are several possibilities on the supply side starting from a simple diode supply unit up to highly sophisticated active IGBT supply units. Multidrives can be used wherever several motors form part of a single process. They come with a common DC bus arrangement, enabling single power entry for several drives. The energy circulating over the common DC bus results in energy and cost savings, as not all energy is taken from the supply network allowing the supply unit in the drive to have smaller dimensions. A single power line connection and a common supply unit reduces the need for cabling and floor space, saving investment and maintenance costs.
[image: ]
[bookmark: _Toc133317113]Figure 9 - Illustration of Multidrive
[2]

The image below in fig ?? shows a suite of cubicles for a multidrive system, the suite is split into two separate section, the supply units and the drive units. The supply units consist of an incomer followed by isolators and an MCB, then an active front end input bridge. The supply will be a three-phase supply, and the AFE will then convert it to DC and supply the DC bus.
The drive unit consists of the inverter modules to drive the individual motors, in the image below some cubicles have two inverter modules which are controlling separate motors, but it is possible to have one drive controlling multiple motors. The inverter modules will switch the DC back to AC ready to supply the motors. It is in the inverter modules where the frequencies are altered, this then changes the speed at which the motor turns.
The multidrive system is excellent because it has the facility to include spare drives in the cabinets, so if there is a fault on one of the drives, the spare one can be switched in, allowing for the maintenance to be planned for when production levels are low, i.e. on a plant stop day. [2]
[image: ]
[bookmark: _Toc133317114]Figure 10 - Multidrive Suite
[2]






[bookmark: _Toc133317147]2.2.3 Motor C - Conveyor
	
	Schneider VFD Drive
	ABB VFD Drive
	Mitsubishi VFD Drive
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	Type
	Altivar Process ATV900
	ACS880-01 Wall Mounted
	FR-A840-00310-E2-60

	Voltage
	380...480 V - 15...10 %
	380 to 415V
	400V

	Power
	15.0 kW for normal duty 
11.0 kW for heavy duty
	1.5 to 6000kW
	11kW

	Variable Speed
	Yes
	Yes
	Yes

	Protection
	Against exceeding limit speed: drive
Against input phase loss: drive 
Break on the control circuit: drive 
Input phase breaks: drive 
Line supply overvoltage: drive 
Line supply undervoltage: drive 
Overcurrent between output phases and earth: drive 
Overheating protection: drive 
Overvoltages on the DC bus: drive 
Power removal: drive Short-circuit between motor phases: drive 
Thermal protection: drive Motor phase break: motor 
Power removal: motor 
Thermal protection: motor
	• Safe torque off (STO) 
• Safe stop 1 (SS1-t and SS1-r) 
• Safe stop emergency (SSE) 
• Safe brake control (SBC) 
• Safely-limited speed (SLS) 
• Safe maximum speed (SMS) 
• Prevention of unexpected startup (POUS) 
• Safe direction (SDI) 
• Safe speed monitor (SSM) 
• Safe motor temperature (SMT)
	

	Reversable Motor Direction
	Yes
	Yes
	Yes

	Operating Temperature
	-15…40 °C (without derating) 
40…50 °C (with derating factor)
	0°C to 50°C
	0°C to 50°C

	Degree of Protection
	IP55
	- IP22 Standard
- IP42 & IP 54 Options
	IP55

	Connectivity
	Slot A: communication module for Profibus DP V1 
Slot A: communication module for PROFINET 
Slot A: communication module for DeviceNet 
Slot A: communication module for EtherCAT 
Slot A: communication module for CANopen daisy chain RJ45 
Slot A: communication module for CANopen SUB-D 9 
Slot A: communication module for CANopen screw terminals 
Slot A/slot B/slot C: digital and analog I/O extension module 
Slot A/slot B/slot C: output relay extension module 
Slot B: 5/12 V digital encoder interface module 
Slot B: analog encoder interface module 
Slot B: resolver encoder interface module communication module for Ethernet Powerlink
	- 2 Analogue inputs
- 2 Analogue outputs
- 6 Digital inputs
- 3 Relay outputs
- Safe Torque off
- Drive to Drive link (EIA 485)
- Built in Modbus
- Assistant control panel (RJ45)
- Bluetooth
	128 (input: 64 points
output: 64 points) 19 points built-in (input: 12 points, output: 7 points)
FR-A8AX (input: 16 points) FR-A8AY (output: 7 points)
FR-A8AR (output: 3 points)
3 input points built-in (Terminals 1, 2, and 4)
FR-A8AZ: 1 input point (Terminal 6)
2 output points built-in (Terminals F/C(FM/CA) and AM)
FR-A8AY: 2 output points (Terminals AM0 and AM1)
FR-A8AZ: 1 output point (Terminal DA1)

	Price
	
	
	


[bookmark: _Toc133317132]Table 5 - Conveyor System
The Conveyor system will be controlled by 3 Wall mounted ACS880-01-302A-5 which will be housed inside control panels in a nearby contactor room. There is a total of 23 motors on the conveyor all operating at the same speed so one drive will control 12 motors and one drive will control 11 motors.
Each VFD respectively will need to control multiple motors so there should an extra 10% added on when selecting the  kW rating of the drive.
Drive 1 10kW x 12 motors = 120kW + 10% = 132kW
Drive 2 10kW x 11 motors = 110kW + 10% = 121kW
The ACS880-01-302A-5 shown in fig ?? has a kW rating of 132kW so this will be used for both drive 1 & 2 and the spare drive so that there is interchangeability and commonality of spares.
The three drive’s parameters will be set up identically and normal operation will be to use the two drives and have the spare in standby so that it can be switched in remotely to prevent downtime on the conveyor. This will be done by switching a contactor arrangement supplying the drives.
[image: ]
[bookmark: _Toc133317115]Figure 11 - ACS880-01 Specifications
[3]



[bookmark: _Toc133317148]2.2.4 Motor D - Cutting Machine
	
	ABB Soft Starter
	Telemecanique Soft Starter
	Schneider Altivar ATS480
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	[bookmark: _Hlk133141153]Type
	PSR12
	ATS01N222LU
	Altivar ATS480

	Voltage
	208...600 V +10%/-15%, 50/60 Hz ±5%
	200….240V AC
	208...690 V - 15...10 %

	Power
	5.5kW
	5.5kW
	7.5 kW at 400 V in the motor supply line normal duty
 5.5 kW at 400 V in the motor supply line heavy duty

	Variable Speed
	Yes
	Yes
	Yes

	Protection
	External Switch fuse and thermal overload relay
	External Switch fuse and thermal overload relay
	Phase failure: line 
Integrated thermal protection: motor 
Thermal protection: starter 
Current overload: motor 
Underload: motor 
Excessive starting time, locked rotor: motor 
Motor phase loss: motor 
Line supply phase loss: line
Line supply phase loss: motor
Thermal protection: motor

	Reversable Motor Direction
	No
	No
	NO

	Operating Temperature
	-25...+60 ºC
	-10...+40 ºC
	40…60 °C (with current derating of 2 % per °C) -15…40 °C (without derating)

	Degree of Protection
	IP20
	IP20
	IP20

	Connectivity
	Output signal relays
	n/a
	Communication module for Profibus DP V1
Communication module for PROFINET
Communication module for Modbus TCP/EtherNet/IP
Communication module for CANopen daisy chain
Communication module for CANopen Sub-D
R1A, R1C, R3A, R3C : Sequence relay 
STOP, RUN, DI3, DI4 : Digital inputs 
AQ1 : Analogue output
PTC1/AI1, PTC2, PTC3 : PTC or PT100 connection 
DQ1, DQ2, DQ+ : Digital outputs

	Price
	£203.92
	£291.88
	£743.18


[bookmark: _Toc133317133]Table 6 - Cutting Machine System
The system controlling the cutting machines does not have to be reversed or run at different speeds but does have to be switched on and off at different times. One VFD would not be suitable for this application so it would be costly to install 17 drives.  To save on cost the Schneider Altivar ATS480 soft start unit has been selected. There will be 17 soft start units so each motor can be controlled individually. The motors are relatively small at 5kW but the soft start allows the current to be limited so that no expensive PLC system would need to be installed to prevent all 17 starting at the same time.
The Altivar ATS480 although being slightly more expensive than other soft start units has good motor protection built in so would not need more external equipment to be installed. It also has good communication input/outputs so that the plant can track usage of data such as machine running hours. This can be used to predict when the next planned maintenance is carried out. 

[bookmark: _Toc133317149]2.2.4 Motor E - Pumps / Fans
	
	Schneider
	Newlec NLSTM
	RS PRO DOL
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	Type
	Direct online starter
	Direct online starter
	Direct online starter

	Voltage
	220/230 V AC 50/60 Hz
	230V
	240V

	Power
	2.2 kW
	5.5kW
	1.1kW

	Variable Speed
	No
	No
	No

	Protection
	n/a
	n/a
	n/a

	Reversable Motor Direction
	No
	No
	No

	Operating Temperature
	-5 to +40°C
	n/a
	-5 to +40°C

	Degree of Protection
	IP65
	IP55
	IP55

	Connectivity
	n/a
	n/a
	n/a

	Price
	£52.06
	£123.15
	£80.15


[bookmark: _Toc133317134]Table 7 - Pumps / Fans System
The system which controls the 1kW pumps and fans will be individually started by a direct online starter the reason being that there will be low start up and running current with these motors. Due to the system consisting of 127 small motors there will be individual motor protection unit offering short circuit and overload protection. There will also be a small contactor in line with the direct online starters to enable remote starting the coil of this contactor will be 24V DC and these will be controlled via a PLC.
The code in the PLC  will enable the fans and pumps to switch on when they are required and also prevent a high quantity of motors starting simultaneously causing a current spike in the system. 
The one chosen was the RS PRO DOL because of the amount in service on plant if any failures were to occur this offers next day delivery and holds a large quantity on stock. It was also the mid-range for cost.
[bookmark: _Toc133317150]2.3 Conclusion

The majority of the drive control systems selected were manufactured by ABB the main reasons for this are as follows:
· Achieved a discounted cost due to purchasing more equipment with the same supplier.
· The maintenance teams would have better familiarity working on one type of drive reducing the need for extra training across different drives.
· Only required to purchase one drive software package.
· Would be able to stock spares which would be compatible in different areas of plant again saving costs.
An active front end was used on the gantry crane this will make this system much more efficient. This is due to the amount of times the motors on the crane will be regenerating when electrical braking after almost every movement. The active front end will discharge any unwanted power back onto the grid instead of being dissipated through a braking resistor.
[bookmark: _Toc133317151]3.0 Task 2

[bookmark: _Toc133317152]3.1 Research

‘’VFDs can reduce the starting inrush current and kVA to half of that of an across-the-line starter. The reduction of inrush current in an electrical distribution system has a number of advantages. Many utilities require some form of reduced voltage starting for all motors over 25 hp. On the downside, VFDs utilize silicon controlled rectifiers to chop up the ac waveform and will provide a nonlinear waveform. This nonlinear waveform will cause voltage distortion across the reactor of the generator or the utility transformer and can cause unacceptable transient performance. This will adversely affect the performance of the entire electrical system’’.[4]
‘’The combination of linear and nonlinear loads fed from a common power source can have a significant effect on the electrical distribution system. In situations where mostly linear loads are connected, a pure sinusoidal waveform current can flood the system with fundamental current. Significant linear load in the system will negate the effect of the nonlinear load. A system with primarily nonlinear loads will display a more distorted waveform at the power source’’.[4}

‘’All voltage-source-inverter-based VFDs have an ac to dc rectifier unit with a large dc capacitor to smooth the voltage ripple. The dc bus capacitor draws charging current only when it is discharged into the motor load. The charging current flows into the capacitor when the input rectifier is forward biased. This occurs when the instantaneous input voltage is higher than the dc voltage across the dc bus capacitor. The pulsed current drawn by the dc bus capacitor is rich in harmonics because it is discontinuous. The voltage harmonics generated by VFDs are due to the flat-topping effect caused by a weak ac source charging the dc bus capacitor without any intervening impedance. The distorted voltage waveform gives rise to voltage harmonics, which is of more importance than current harmonics. The reason is simple. Voltage is shared by all loads and it affects all loads connected in an electrical system. Current distortion has a local effect and pertains to only the circuit that is feeding the nonlinear load. Non-sinusoidal currents that draw from the ac source cause undue stress on power delivery equipment that results in poor overall efficiency’’.[4]
‘’By its nature, the VFD is a nonlinear load in the electrical system in the sense that it draws a non-sinusoidal current even if the applied voltage is perfectly sinusoidal. Modern VFDs are designed to minimize this nonlinearity by providing multi-pulse (12-, 18-, and 24-pulse) line converters, active front-end converters, or passive harmonic filters and line reactors at the input. Despite this, harmonic currents flow in electrical systems subjecting other equipment to non-sinusoidal voltages. Symptoms of serious harmonic problems are:
· Overheating of transformers, motors
· Incorrect operation of electronic instruments and various types of sensors and meters
· Excessive current in and failure of power factor correcting capacitors
· premature failure of circuit breakers’’.[4]
‘’Utility power harmonics are generated when a load draws nonlinear current from a sine wave voltage source. Harmonics are defined from the Fourier series that defines any periodic wave shape. Typically a three-phase, six-pulse VFD will draw nonlinear current that introduces the fifth and seventh harmonics on top of the fundamental frequency. A single phase, four-pulse VFD will produce the third harmonic or “triplen” harmonic. The symptoms of the VFD related harmonics are evident as a distorted line voltage. This harmonic voltage distortion can disrupt or stop operation of sensitive equipment’’.[4]
An example of how variable frequency drive harmonics can affect the supply is shown in fig 11.
[image: ]
[bookmark: _Toc133317116]Figure 12 - Harmonics Graph
[5]
[bookmark: _Toc133317153]3.2 Harmonic Noise

When using non-linear loads such as Variable frequency drives unwanted frequencies are created. These frequencies which are much higher than the 50Hz supply will potentially be turned into heat due to them not being consumed by the appliance or the machine. 
There are a variety of different technologies which have the ability to reduce these effects. Some examples of these are:
· Install higher rating transformers
· Smaller impedance in supply transformer
· More pulses in the rectifier
· Larger short circuit capacity of supply
· Connect filters into the circuit
· Drives with bigger DC inductors
Also another way is by rectifying the incoming mains using Diodes, Silicon controlled rectifiers (SCRs) or Insulated gate bipolar transistors (IGBTs).


[bookmark: _Toc133317154]3.3 Proteus Simulations

The circuit in figure 12 is constructed using diodes.

[image: ]
[bookmark: _Toc133317117]Figure 13 - Circuit 1 (Diode)
Analogue probes were placed on the incoming supply and on the output this data was used to make the graph in figure 13. Also in figure 14 demonstrate

[image: ]
[bookmark: _Toc133317118]Figure 14 - Analogue Analysis of Circuit
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[bookmark: _Toc133317119]Figure 15 - Fourier Analysis

As an improvement transformers were added with star-delta and star-star coniguration was constructed as shown in figure 15 & 16.


[image: ]
[bookmark: _Toc133317120]Figure 16 - Star Delta Configuration
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[bookmark: _Toc133317121]Figure 17 - Star Star Configuration
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[bookmark: _Toc133317122]Figure 18 - Line Analysis Graph
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[bookmark: _Toc133317123]Figure 19 - Line Analysis Graph
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[bookmark: _Toc133317124]Figure 20 - Line Analysis Graph
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[bookmark: _Toc133317125]Figure 21 - Load Analysis Graph
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[bookmark: _Toc133317126]Figure 22 - Load Analysis Graph
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[bookmark: _Toc133317127]Figure 23 - Load Analysis Graph

The circuits were then constructed on Proteus using silicon controlled rectifiers (SCRs) and insulated gate bipolar transistors (IGBTs). Unfortunately there was an issue with these circuits and the graphs and data could not be gathered.

[bookmark: _Toc133317155]3.4 Conclusion













[bookmark: _Toc133317156]4.0 Datasheets

ABB ACS880 ACS880-107 Inverter modules (INU) - ACS880 multidrives (Industrial drives - unlimited possibilities for your business) | ABB
Schneider AT480 https://www.se.com/uk/en/product/download-pdf/ATS480D17Y
ABB PSR 12 https://docs.rs-online.com/63fb/0900766b8138b45b.pdf
RS Pro 1.1KW DOL Starter https://docs.rs-online.com/098a/0900766b81586117.pdf
Schneider ATV61Q https://www.se.com/ww/en/product/download-pdf/ATV61QC50N4
Schneider ATV900 https://www.se.com/ww/en/product/download-pdf/ATV950D15N4U
Vacon NXP0168 https://www.quantum-controls.co.uk/wp-content/uploads/product-sheets/variable-speed-drives/vacon/NXP/NXP-operating-guide.pdf
Allen Bradley Power Flex 750-Series PowerFlex 750-Series AC Drives Technical Data (rockwellautomation.com)
VYBO V810 Variable frequency drive 500kW 400V V810 VYBO Electric - VYBO Electric
Mitsubishi FR-A840 https://www.quantum-controls.co.uk/wp-content/uploads/product-sheets/variable-speed-drives/mitsubishi/A800/a800-catalog.pdf
Telemecanique ATS01N222LU https://www.se.com/ww/en/product/download-pdf/ATS01N222LU
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Type Code Frame ‘Output Ratings Noise Heat “Air flow
size Light duty Heavy duty level  Loss(kw)  (cfm)
L) P M) P, L. P, P, (48R
kW) (A) (Hp) (kw)
U, =500V (range 380 to 500V). Power ratings are valid at nominal voltage 480 V 60 Hz
6 E"E diode Md: rectifier

'ACS880-07-0096A-5+C129. RE 9% 15 55 1760 45 67 18 838
ACS880-07-0124A-5+C129 RE 124 100 75 96 75 55 67 194 838
ACS880-07-0156A-5+C129 RT 156 125 9 124 100 75 61 244 838
ACS880-07-0180A-5+C129 RT 180 150 110 156 125 90 67 281 838
ACS880-07-0240A-5+C129 R8 240 200 180 150 110 67 838
ACS880-07-0260A-5+C129 R8 260 215 160 240" 200 132 65 838
ACS880-07-0302A-5+C129 ) 302 250 200 260 200 132 68 551
ACS880-07-0361A-5+C129 (5] 361 300 200 302 250 200 68 551
ACS880-07-0414A-5+C129 [ 414 350 250 361°* 300 200 68 551
ACS880-07-0460A-5+C129 RI0 as0 375 315 330 215 200 72 1413
ACS880-07-0503A-5+C129 R10 483 a00 315 361 300 250 72 1413
ACS880-07-0583A-5+C129 RI0 573 as0 400 414 350 250 72 1413
ACS880-07-0635A-5+C129 R10 623 500 450 477400 315 72 1413
ACS880-07-0715A-5+C129 R11 705 600 500 566 450 400 72 1413

[acs880-07-08804-5+C129

ACS880-07-1320A-5+C129+F255+H359'

2xDBTe2xR8I 1267 1000

200
ACS880-07-1450A-5+C129+F255+H350'" 2xDBT+2xR8I 1392 1200 900 1085 900 710 74 258 2740
ACS880-07-1580A-5+C129+F255+H359'> 2xDBT+2xR8I 1517 1250 1000 1182 1000 800 74 27 2740
ACS880-07-1800A-5+C129+F255¢H359'> 2xDBT+3xR8I 1728 1500 1200 1346 1100 900 75 32 3425
ACSB80-07-1980A-5+C129+F255+H359'% 2xDBT+3xR8I 1901 1500 1300 1481 1250 1000 75 36 3425
12-pulse connection

ACS880-07-0990A-5+A004 +H359. 2xD7T+2xRBI 950 800 €30 741 600 500 73 16 2740
ACS880-07-1320A-5+A004+H359. 2xDBT+2xR8I 1267 1000 900 987 900 710 74 22 2740
ACS880-07-1450A-5+A004+H359 2xDBTe2xR8I 1392 1200 900 1085 900 710 7 25 2740
ACS880-07-1580A-5+A004+H359. 2xDBTe2xR8I 1517 1250 1000 1182 1000 800 74 27 2740
ACS880-07-1800A-5+A004+H359. 2xDBTe3xR8I 1728 1500 1200 1346 1100 900 75 32 3425

ACS880-07-1980A-5+A004 +H359 2xDBT+3xR8I 1901 1500 1300 1481 1250 1000 75 36 3425
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Frame  Light Duty use

size 1, P P P,  Level Loss cfm
A Hp. kw A Hp. kw Bl we
U, = 500V (range 380 to 500 V). Ratings are valid at nominal voltage 480 V, 60 Hz
ACS880-01-02A1-5 R 2.1 1 ors 17 015 055 50 a2 26
ACS880-01-03A0-5 Rl 3 15 11 21 1 015 so s0 26
ACS880-01-03A4-5  R1 34 2 15 3 15 11 0 ss 26
ACS880-01-08A8-5 Rl a8 3 22 34 2 15 0 7 26
ACS880-01-07A6-5 R1 6 B 4 s2 3 3 s0 1m0 2
ACS880-0111A0-5 R 1 5 55 6 s 4 s0 180 26
ACS880-01-014A-5 R2 14 10 15 1 75 55 s 191 s2
ACS880-01-021A-5 R2 2 15 1 14 10 5 s 330 s
ACS880-01-027A-5 R3 2 20 15 2 15 1u 60 326 19
ACS880-01-034A5  R3 34 25 185 21 20 15 60 asa 19
ACS880-01-040A-5 R4 40 10 22 34 25 185 64 42819
ACS880-01-052A5 R4 s2 40 30 40 30 22 6 600 165
ACS880-01-065A-5 RS 6s 50 3 s2 40 30 6 715 165
ACS880-01-077A-5 RS [ 60 as 65 50 £ 64 96 165
ACS880-01-096A5  R6 % 75 55 7 60 s 8 157 256
ACS880-01-124A-5 R 124 100 15 % 5 s5 68 1673 256
ACS880-01-156A-5 R7 156 125 90 124 100 15 67 1840 265
ACS880-01-180A-5 R7 180 150 110 156 125 90 67 2281 265
ACS880-01240A-5 RS 240 200 132 180 150 110 68 2012 324
T ——— €

ACS880-01-414A-5 Rr9 a1 350 250 361 300 200 10 se12__err

" Heat Loss value = a reference for cabmet thermal design. Value i calculated to Ecodesign reguiations based on 90% speed and 100% current
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Block diagram for a variable
frequency drive (VFD)

AC ——> DO ————>ACCPWM)
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