| LOCATION: Swansea | LLEOLIAD: abertawe |
| --- | --- |
| LEVEL 7 | LEFEL 7 |
| EXAMINATION PERIOD | CYFNOD ARHOLIADAU |
| may 2016 | mai 2016 |

MODULE CODE: M7X11112

WATER TREATMENT TECHNOLOGY

TIME:  2.0 HOURS

answer all questions

Equipment or materials required – None

Adnoddau neu ddefnyddiau sydd eu hangen - Dim

ANSWER ALL QUESTIONS

Question One (25 marks)

- In brief, compare the properties and characteristics of ground water and surface water?

(8 marks)

- The results of laboratory tests carried out on the water quality of the treated water in a water treatment plant before supply to the customers are as follows:

1 - Colour 	18 units (PCU)

2 - Turbidity   	7.5 NTU

3 - PH		10.2

Explain in brief whether or not the treated water is fit for human consumption as drinking water.

(7 marks)

- Find the hardness of water that has a Ca2+ concentration of 70mgLas ions    and a Mg2+concentration of 9.7mgL as ions.

(10 marks)

Question Two (25 marks)

- A pre-sedimentation tank is to be designed to treat a maximum flow rate of 60,000 m3/d of surface water.  The target particle for settling has the following characteristics: average diameter  ds = 200×10-6m, cohesion constant k=0.05, Daracy-Weisbach friction factor f = 0.025, and density ρs = 1.25×103kg/m3.

The viscosity of water is 1.003×10-3kg/ms and its density is ρl=1.0×103kg/m3.  G is the acceleration due to gravity (9.81m/s2).

For a rectangular classifier having length to width ratio of 6, the overflow rate is at least four times the settling velocity and the horizontal velocity is at most one-third of the scour velocity.

- Find the dimensions of the rectangular tank.

(ii)  Determine the detention time.

(15 marks)

- Explain in brief, using schematic diagrams, the difference between an Aerobic ground water treatment plant and a deep anaerobic groundwater treatment plant.

(10 marks)

Question Three (25 marks)

- A rapid mixer of square cross section is to be used for coagulation of surface water with high turbidity.  If the flow is 720m3/h finds the volume and dimensions of the tank and the power requirements.  Assume that the detention time is 30 seconds and the mean velocity gradient G = 1000S‐1.  The viscosity of water μ = 1.518 x 10‐3N.m/s2 at 5oC.

(10 marks)

- A dual media filter is composed of 0.30m anthracite (mean particle size 0.20mm) that is placed over a 0.60m layer of sand (mean particle size 0.70mm) with a filtration rate of 9.78m/h.  Assuming the grain sphericity ф = 0.75 and porosity (ε) = 0.40 for both, estimate the head loss in the clean filter at 15oC.

(7.5 marks)

- Briefly describe the different classifications of the membrane processes used in water treatment.

(7.5 marks)

Question Four (25 marks)

- The molar concentrations of the major ions in a brackish ground water supply are as follows:

Na+, 0.02;Mg2+, 0.015;Ca2+, 0.01;K+, 0.001; Cl-, 0.025; HCO3-, 0.001;NO3-, 0.002;

and SO42-, 0.012

What would be the approximate osmotic pressure difference across a semipermeable membrane that has brackish water on one side and mineral-free water on the other, assuming the temperature is 25 degrees centigrade?  How much pressure needs to be applied on the brackish water side to increase the mineral-free water content?

(10 marks)

- 1 - Explain in brief the principle of Electrodialysis water treatment process.

2 - What are the major limitation of the ozonation process?

(8 marks)

- Referring to the Figure below, if a dosage of 1.8mg/L of chlorine is applied to disinfect water in water treatment plant, determine:

- The amount free chlorine residual.

- The amount of combined residual.

- The amount of total residual.

- The chlorine demand?

(7 marks)

Diwedd/End

Physical Characteristic of standards water

Maximum horizontal velocity VH=8kf(ρs-ρl)ρlgds

vt=gD218μ(ρs-ρl)    Stokes law

Re=ρvtDμ

P=μVG2

V = Qxt

hL=kμ1-ε2gρε3(VA)2v

VA=6∅d

π = cRT

R = Universal gas constant 0.08206 L.atm/K.mol