Measuring the load, we get:

- Wattmeter reading = 3.6 kW

- Ammeter reading = 20.7 A RMS

Correct the power factor to 0.9

Step 1 – Calculate S

S = VI = 230 x 20.7 = 4761 VA

Step 2 – Calculate power factor

pf=36004761=0.756

Step 3 – Calculate new phase angle

φ=cos-1pf

NEWpf=cosφ=0.9≈25.84°

Step 4 – Calculate New reactive Power

New reactive power = Real power x tanφ = 3600 x tan(25.84) = 1743.4097 VAr

Step 5 – Calculate change in reactive power

Change in reactive power = 4761-1743.4097 = 3017.5903 VAr

Step 6 – Calculate capacitive reactance needed for this change in reactive power

Q=V2X

X=V2Q=23023017.5903=17.5305 Ω (Cap)

Step 7 – Calculate required capacitor value

XC=12πfC

C=12πfX=181.57μF