Monitoring of Street Lighting at Pembrokeshire County Council to verify that the Part Night switching policy is being implemented correctly

by

Matthew Williams

Supervisor: Dr Stephen Mosey

Second Marker: Jenifer Prince Devaraj

Project submitted as part of the requirements for the award of BEng (Hons) Electrical and Electronics Engineering

April 2025

# Abstract

This project aims to verify if the Part Night (PN) switching policy at Pembrokeshire County Council (PCC) is being implemented properly. The PN policy aims to reduce energy costs for the authority by switching off most of the streetlights in its portfolio during a designated period at night when vehicular traffic and pedestrian usage are at its lowest. This policy is not always popular with the residents of Pembrokeshire and often results in complaints suggesting the lights stay on too long or go off sooner than they are intended to. To accurately deal with these complaints, a reliable monitoring system is needed to verify the switching times of certain streetlights. This report details the development of a PIC Microcontroller based sensor and data collection system designed to record the switching times of tested streetlights. The data collected will then be able to be evaluated and checked against the required switching times set out in the policy. The system will also help by improving value for money through the authority’s maintenance department being able to reject requests to reattend units that are reported as faulty. The data collected will also highlight street lighting units that stay on longer than intended and help to adhere to the authority’s energy saving policy. The monitoring device designed will be both adaptable to all types of streetlights and to other local authorities looking at cost effective monitoring of their systems.

# Declaration Form and Form of Consent

DECLARATION FORM

I, ..........Matthew Williams.......... declare that I am the sole author of this Project; that all references cited have been consulted; that I have conducted all work of which this is a record, and that the finished work lies within the prescribed word limits.

This work has not previously been accepted as part of any other degree submission.

FORM OF CONSENT

I ..........Matthew Williams..........  hereby consent that my Project, submitted in candidature for the BEng (Hons) Electrical and Electronics Engineering degree, if successful, may be made available for inter-library loan or photocopying (subject to the law of copyright), and that the title and abstract may be made available to outside organisations.

# Acknowledgements

To my supervisor Dr Stephen Mosey, thank you for always being enthusiastic about my choice of project. Your expert advice, constructive feedback and support during all our meetings spurred me on to work outside my comfort zone. I am extremely grateful for both your time and patience. For some people streetlighting may not be the most exciting subject, and yes there were struggles along the way, yet you provided encouragement and understanding that helped me to keep focussed on the road ahead and to complete this project successfully.

To technician Dylan Alame and all the support staff at UWTSD IQ Swansea, thank you for always being eager to help and support during the building of the prototype.

I would also like to thank my whole family, and particularly my wife Jayne. You have all put up with my stresses, frustrations and not to mention all the hours and weekends spent locked away in the office. Despite this, you have all provided huge support and encouragement along the way. If this project is measured by the belief you all have in me and the motivation you give me every day then there’s no doubt this project was always going to be a success.

Diolch

Table of Contents

Abstract	2

Declaration Form and Form of Consent	3

Acknowledgements	4

List of Figures	8

List of Tables	9

List of Equations	9

List of Abbreviations	9

1. Introduction	10

2. Research and Literature Review	12

3. Methodology	17

3.1 Development Methodology	17

3.2 Incremental Methodology	18

3.3 Software	19

3.3.1 Embedded C	19

3.3.2 Proteus	19

3.3.3 CCS Compiler	19

3.4 Hardware	19

3.4.1 PIC Microcontroller	19

3.4.2 Current Transformer	19

3.4.3 GPS Chip	19

3.4.4 Various Electronic Components	19

3.5 Tools	19

3.5.1 PICkit 3	19

3.5.2 Soldering Kit	19

4. Design & Implementation	20

4.1 Design Specification	20

4.2 Output Requirements	20

4.3 Existing Systems	21

4.4 Design Options	23

4.5 The Design	25

4.5.1 Design Parameters	25

4.5.2 Equipment Requirements	25

4.5.3 Current Transformer (CT Clamp) Selection	26

4.5.4 GPS Selection	28

4.5.5 DC-DC Converter Selection	30

4.5.6 Memory Requirements	31

4.5.7 Memory Selection	34

4.5.8 Microcontroller Selection	35

4.5.9 Power Options	39

4.5.10 Power Requirements	40

4.5.11Power Selection	43

4.5.12 Battery Configuration	44

4.5.13 Miscellaneous Components	45

4.6 Circuit Design	48

4.6.1 Power Rail Schematic	49

4.6.2 DC-DC Converter Schematic	51

4.6.3 PIC 16F667 Microcontroller Schematic	51

4.6.4 PIC Decoupler Schematic	52

4.6.5 MCLR Schematic	52

4.6.6 CT Circuit, Amplifier & Rectifier Schematic	53

4.6.7 GPS Schematic	57

4.6.8 LCD Display Schematic	58

4.6.9 EEPROM Schematic	58

4.6.10 Writing to EEPROM LED Schematic	59

4.6.11 Button Assembly Schematic	59

4.6.13 Full Proteus Schematic	60

4.7 The Software	61

4.8 Cost and Figures	65

5. Evaluation & Results	68

5.1 Design and Implementation Overview	68

5.2 Evaluation of the Objectives	69

5.2.1 Objective 1: Design and develop a compact, cost-effective monitoring device using a PIC microcontroller	69

5.2.2 Objective 2: Detect switching ON & OFF events	70

5.2.3 Objective 3: Capture GPS time at switching events	71

5.2.4 Objective 4: Log data to external EEPROM	72

5.2.5 Objective 5: Providing real-time feedback via LCD and LED indicators	73

5.2.6 Objective 6: Enable retrieval of logged data for analysis and feedback	73

6. Conclusions and Recommendations	75

7. Reflection	79

References	81

Bibliography	87

Appendices	88

Appendix A – PCC Street Lighting Policy	88

Appendix B – Streetlighting complaints Examples	92

Appendix C – PCC APSE Benchmarking Results	95

Appendix D – CTA Split Core Current Transformer Datasheet	98

Appendix E – Adafruit Ultimate GPS Datasheet	102

Appendix F – GPS External Antenna Datasheet	113

Appendix G – DC-DC Converter Datasheet	117

Appendix H – EEPROM Datasheet	123

Appendix I – PIC16F887 Microcontroller Datasheet	132

Appendix J – LiPo Battery Datasheet	161

Appendix K – 3.3V Voltage Regulator Datasheet	162

Appendix L – Operational Amplifier Datasheet	171

Appendix M – 5V Voltage Regulator Datasheet	186

Appendix N – Red / Green LED Datasheet	196

Appendix O – LCD Display Datasheet	198

Appendix P – Tactile Buttons Datasheet	208

Appendix Q – Fixed Terminal Block Datasheet	210

Appendix R – Header Pins Datasheet	211

Appendix S – Software Code	215

Appendix T – Additional Part Night Information	219

# List of Figures

Figure 1 Pembrokeshire County Council Carbon Footprint [10]	13

Figure 2 Example of Smart Streetlighting [25]	14

Figure 3 Example of CMS [69]	15

Figure 4 Waterfall Development Methodology [70]	17

Figure 5  Increment Development Methodology [71]	18

Figure 6 PCC types of Streetlights: Traditional over carriageway, Post-Top, Decorative, Wall mounted	23

Figure 7 Chosen Current Transformer - Carlo Gavazzi CTA5X100A5A (Datasheet - See Appendix D) [41]	27

Figure 8 Chosen GPS Receiver - Adafruit 746 (Datasheet - See Appendix E) [43]	29

Figure 9 GPS Antenna (Datasheet - See Appendix F) [72]	29

Figure 10 Chosen DC-DC Converter - RECOM RS3-0515D/H3 (Datasheet - See Appendix G) [48]	31

Figure 11 Chosen EEPROM - Microchip 24LC1026 (Datasheet - See Appendix H) [73]	34

Figure 12 Chosen PIC Microcontroller - PIC16F887 - (Datasheet - See Appendix I) [74]	38

Figure 13 PIC16F887 Block Diagram [75]	38

Figure 14 Chosen Battery – LiPo 10,000mAh - (Datasheet - See Appendix J) [55]	44

Figure 15 Battery Configuration	44

Figure 16 Power Supply Block Diagram	48

Figure 17 Power Supply Schematic - Battery, Battery Metering & 7.4V Supply	49

Figure 18 Power Supply Schematic - 5V Regulated Supply	50

Figure 19 Power Supply Schematic - 3.3V Regulated Supply	50

Figure 20 DC-DC Converter Schematic	51

Figure 21 PIC16F887 Schematic	51

Figure 22 PIC Decoupling Capacitor	52

Figure 23 Master Clear (MCLR) Schematic	52

Figure 24 CT Circuit Schematic - Simulated Switching	53

Figure 25 CT Circuit Schematic - Burden Resistor	54

Figure 26 CT Circuit Schematic - Amplifier	55

Figure 27 CT Circuit Schematic - Rectifier	56

Figure 28 CT Circuit Schematic - Filter	57

Figure 29 GPS Schematic	57

Figure 30 LCD Display	58

Figure 31 EEPROM	58

Figure 32 Green LED Schematic	59

Figure 33 Button Assembly Schematic	59

Figure 34 Full Proteus Schematic	60

Figure 35 Flowchart of the software code	61

Figure 36 Code Extract 1 - Extracting Time from NEMA String	62

Figure 37 Code Extract 2 - Test Screen Function	62

Figure 38 Code Extract 3 - The Menu	63

Figure 39 Code Extract 5 - Clearing the EEPROM Memory	64

Figure 40 Code Extract 4 - Change of State Time Capture	64

Figure 41 LMD System Block Diagram	68

Figure 42 Full Breadboard Prototype	69

Figure 43 Graphical Expression of how CT Signal is Amplified and Rectified	70

Figure 44 Proteus Light ON and OFF Times	71

Figure 45 Light ON and OFF Graph	71

Figure 46 Location of EEPROM on Breadboard	72

Figure 47 Location of GPS Module on Breadboard	74

Figure 48 Proteus Schematic	76

Figure 49 Programming the PIC Microcontroller	77

# List of Tables

Table 1 Tabulated Comparison of Existing Systems [33], [34], [35]	22

Table 2 Tabulated Comparison of Sensor Technology [36], [37], [38], [39]	24

Table 3 Parameters to Measure	25

Table 4 Current Transformer Comparison [40], [41], [42]	27

Table 5 GPS Receiver Comparison [43], [44], [45]	29

Table 6 DC-DC Converter Comparison [46], [47], [48]	30

Table 7 NMEA-0183 Output Messages	31

Table 8 GGA Data Format	32

Table 9 Parameter Values	33

Table 10 No. of Bytes required for each write to memory	33

Table 11 Frequency of Measurement	33

Table 12 Total Non-Volatile Memory required for 7 day Operation of Light Monitoring Device	34

Table 13 Type of Output from Device	35

Table 14 Number of IO Pins required for PIC Microcontroller	35

Table 15 PIC Microcontroller Comparison [49]	37

Table 16 Tabulated Comparison of Power Sources [50], [51], [52]	40

Table 17 Power Demand of Device	41

Table 19 Battery Comparison [53], [54], [55]	43

Table 20 Miscellaneous Components (#1)	45

Table 21 Miscellaneous Components (#2)	46

Table 22 Miscellaneous Components (#3)	47

Table 23 Prototype Bill-of -Quantities	67

Table 24 Evaluation of Objectives	73

# List of Equations

Equation 1 Memory Required for 7-Day Logging	34

Equation 2 Battery Power Calculations	44

Equation 3 Voltage Divider Calculations	49

Equation 4 Simulation of Light ON and OFF Calculations	53

Equation 5 Burden Resistor Calculations	54

Equation 6 Circuit Gain Calculation	55

Equation 7 LED Resistor Value Calculation	59

# List of Abbreviations

CT	Current Transformer

IoT	Internet of Things

IP 	Ingress Protection

LDR	Light Dependent Resistor

LMD	Light Monitoring Device

PCC	Pembrokeshire County Council

PN	Part Night

# 1. Introduction

Streetlighting is an important component of any local authority’s highway infrastructure, [1] crucial for both increasing public safety and increasing road visibility. Local authorities are continuously attempting to balance the provision of essential public services with the importance of reducing energy consumption and operational costs, so rethinking innovative and different lighting and control systems is increasingly essential whilst continuing to provide a service that the public demand. One method is the adoption of part-night switching policies, which consists of extinguishing or dimming streetlights during designated periods of low activity, usually in the late-night and early-morning hours. This method conserves energy and diminishes carbon emissions, helping to achieve environmental sustainability goals. PCC’s PN policy was implemented in 2008 and states that lights will be extinguished for 5 ½ hours a night, typically from midnight to 5:30am “see Appendix A”.

The basic problem this project attempts to address is the lack of a robust system to verify that the PN switching policy is being correctly implemented across Pembrokeshire's street lighting network. Customer complaints regarding specific lights not working correctly tends to be subjective in nature, as they want it to be on when carrying out some tasks. For example, the light outside their home may not be on when they are going to work, but the light down the road is, there are many reasons why this may not be on yet, e.g. shading, power cut in the area “see Appendix B”.

Corporate Complaints are having to be upheld due to the lack of evidence that the streetlight in question may well be working within its intended parameters. Historically, monitoring was carried out by night inspectors to verify such complaints. Unfortunately, these have now been lost due largely to austerity measures and budget constraints.

To address this issue of corporate complaints, the primary aim of this project is to design and develop a device that can be used across the PCC Streetlighting network to log the switching on and off times, to answer the question of “does this streetlight comply with PN switching policy?” The monitoring device can then be used to show evidence and to give detailed information to members of the public who have raised concerns or complaints about specific streetlights, in the hope of being able to reject corporate complaints and improve the authority’s KPIs.

Below are the objectives of the project, that will, if implemented correctly, satisfy the aim of the project:

- Design and develop a compact, cost-effective monitoring device using a PIC microcontroller that can be easily installed on the existing street lighting network.

- Capture streetlighting switching ON & OFF times

- Real-time feedback via LCD and LED indicators

- Data Logging of the switching on and off times of the streetlight that needs examining. This data will need to be stored for analysing later.

- Data Retrieval of the logged data needs a user-friendly interface for analysing the data and reporting it to members of the public.

This report will provide a comprehensive overview of each stage of the project. Detailing the research and implementation of the design and development of the monitoring device and hopefully, by the end, will show how it can help PCC to determine if its PN switching policy is being implemented correctly, and will contribute to improved customer satisfaction.

# 2. Research and Literature Review

Electric street lighting has been a feature of urban and sub-urban settlement since the end of the nineteenth century. Indeed, the electriﬁcation of lighting has in many ways deﬁned the modern city, in extending the visibility of its public spaces, inhabitants and itinerants beyond the hours of natural daylight [2].

Cost effective and environmentally friendly street lighting plays a crucial role in the modern highway infrastructure of any Local Authority. Assisting in both safety for road users and residents’ wellbeing. Streetlighting technologies dating back to the 1960s were one of the largest energy drains for Local Authorities in the UK, amounting to approximately 40% of their total electricity consumption [3]. PCCs first step towards reducing their energy costs came in 2008 with the implementation of PN switching of their street lighting infrastructure. This was followed with a secondary step towards reducing energy costs and carbon footprint when further reductions were made when the authority followed cities worldwide in replacing its traditional lamps with LEDs [4].

PN switching of streetlights, is a system used by many local authorities to reduce energy consumption and carbon emissions, particularly in residential areas, where traffic accidents and crime rates are significantly lower [3]. Turning of streetlights also mitigates light pollution and the amount of light energy radiated into the sky [5].

The implementation of part night switching policies varies depending on the local authority involved and the needs of its residents. The needs of a rural county like Pembrokeshire are very different to the needs of say a city council like Swansea, even though the type of lights used may be very similar. Typically, streetlights are either extinguished or dimmed during the hours between midnight and 5am [3], [6], [7].

This reduces the number of hours during which streetlights are operating at full capacity. The main objective of part night switching is to strike a balance between reducing energy costs and ensuring public safety. Local authorities are also mindful of residents' concerns and the potential negative impacts on public security during these hours [2], [8]. For example, in the UK, many local authorities, including Hertfordshire, Shropshire, Buckinghamshire as well as Pembrokeshire have all adopted part night switching as part of their street lighting policies. These councils have often cited cost savings as a key driver for the change [2]. Some authorities, fearing the backlash of its residents have opted for investment in LED lighting, which can be dimmed as opposed to switched off completely.

Cost savings are not the only considerations for local authorities when implementing Part Night Policies. With streetlighting accounting for approximately 8% of environmental pollution due to greenhouse gas emissions [9], reducing the operation of streetlights during low-traffic hours lowers energy consumption and leads to a decrease in carbon emissions. As part of the UK's commitment to reducing carbon emissions, part night switching supports national goals to transition to a greener, more energy-efficient society [1].

PCCs has reduced its carbon emissions from its streetlighting by 60% since introducing PN switching in 2008. From 2,220 tCO2e to 886 tCO2e [10].

Figure 1 Pembrokeshire County Council Carbon Footprint [10]

As well as reducing costs, energy and carbon footprint, PN policies also help with ecological factors. Dark skies policies aim to reduce the effect of artificial night-time lighting on nocturnal species. PN lighting can help by reducing sky glow and pollution that may be harmful to these wildlife species [11].

Despite the implementation of PN policies across the country, and the advantages it has for local authorities, residents have numerous concerns regarding its introduction. Public concerns centre on personal security, road safety, crime, fear of crime, sleep quality and generally feeling unsafe after dark [12]. However, a report funded by the National Institute for Health Research found that where street lighting data that was obtained from 62 local authorities, there was no evidence that reduced street lighting was associated with road traffic collisions at night [13]. There was, however, significant discrepancy in the estimated effects on crime at police force level. Overall, there was no evidence that part nighting of streetlighting was associated with increased levels of crime [8].

High quality public services are increasingly being demanded by municipal residents [14]. Local authorities (LAs) are increasingly using customer satisfaction surveys to assess their performance, and this information can be used to drive service improvements. However, it's important to note that the public may not always be aware of funding cuts and reductions in resources faced by the local authority, which can affect their satisfaction levels [15]. Benchmarking is a key component of performance management for local governments. It involves comparing an organization's performance against that of others to identify areas for improvement. Benchmarking can focus on a range of performance indicators, including cost, quality and customer satisfaction [16]. There are several UK benchmarking schemes in England and Wales, however, PCC use APSE benchmarking, through its "Performance Networks" service. APSE allows local authorities across the UK to compare their performance in various frontline service areas, including streetlighting, by sharing data on KPIs, enabling them to identify areas for improvement by benchmarking against other participating councils, essentially learning from best practices within the sector. APSE performance networks are the largest public sector benchmarking service in the UK. It enables more than 200 local authorities across England, Northern Ireland, Scotland and Wales to share information and manage performance [17].  “See Appendix C”.

Within the last decade, research towards intelligent and sustainable technologies, along with smart city initiatives has attracted significant attention among the scientific community [18].

Streetlighting has evolved beyond recognition since William Murdoch invented gas lighting in the late 18th century, and the first 13 known streetlights were installed along Pall Mall, London in 1807 [19]. Since then, we have seen several advancements in technologies, firstly in the early 1900s when Thomas Edison’s Incandescent Lamps were first used, and during the 20th century, progressions to the use of Mercury Vapour Lamps, Sodium, Metal Halide to recent LED technology [20].

Modern technology doesn’t just concentrate on what equipment illuminates the road. Advancements in research now looks at the way streetlighting operates from a network point of view [21]. The result of this type of study has been the introduction across the industry of systems like:

- Smart Streetlighting

- Internet of Things (IoT)

- Central Management Systems (CMS)

Smart Streetlighting systems are set up to dynamically adapt streetlighting levels and operation to suit the actual conditions of the environment. Typically, streetlighting columns are networked together to a controller which can adjust lighting according to readings from an array of sensors, these can include Light Sensors, Infrared, Cameras. These sensors measure the flow of traffic, pedestrian movement lighting levels and weather conditions [22], [23]. Smart streetlights have the capability of lighting up lamps in the immediate locality around the pedestrian or vehicular movement, while dimming the ones around them and switching off as movement passes through [24].

Figure 2 Example of Smart Streetlighting [25]

The main benefit of Smart Streetlighting is the huge energy reductions that are available. Savings of up to 82.99% have been seen in test areas [23].

This technology also has its downsides, high setup costs [25] and complex calculation of energy consumption due to its adaptive nature.

Central Management Systems (CMS) also known as telemanagement, are highly advanced systems used within the streetlighting industry to monitor, control and adjust the whole connected infrastructure with a targeted approach. CMS connected streetlights are typically connected to a wireless router in the middle of the network to form a spider’s web, mesh affect [23] this provides redundancy so if one unit stops working it can latch onto another [21].

Figure 3 Example of CMS [69]

The gateway router then sends the information received from the streetlights on their status to a remote monitoring unit or central server [23]. From here, a streetlighting engineer can access the information received from the lights and adjust them individually [26]. Parameters that can be individually adjusted, include when each individual streetlight turns on or off and by how much to reduce the lamp power. This allows any number of switching events or dimming levels. The CMS also provides other benefits such as fault detection [27].

With all the above advantages of implementing a CMS system, the major disadvantage here is the high initial setup costs [18], meaning that this system is only used by big capital cities and government organisations like SWTRA (Trunk Roads).

Internet of Things (IoT) is not technically a system on its own. IoT refers to the technology being integrated into modern streetlighting systems to enhance efficiency, reduce energy consumption and enable remote monitoring and control [28], through incorporation into Smart Cities in the above two systems. IoT enabled streetlights can incorporate various sensors, including [29]:

- Environmental Monitoring

  - CO2

  - Temperature

  - Humidity

  - Noise Level

  - Light Level

- Data Collection

  - Traffic Motion Data

  - Pedestrian Motion Data

These sensors are used in conjunction with wireless communication technologies like ZigBee, Wi-Fi and LoRaWAN to communicate between lights, control systems and software [30].

Electric Vehicle Charging is now a technology that is being integrated into streetlighting networks, and IoT is playing a big part of the move into this technology [31]. Along with Green technology, and the move towards Solar, Wind and Hybrid lighting, IoT enabled sensor networks are essential components of these green lighting systems, which aim to reduce greenhouse gas (GHG) emissions associated with electricity generation from fossil fuels [18].

Existing technologies as discussed above would be both expensive and difficult to implement, so a more cost-effective solution and standalone option is required in Pembrokeshire.

# 3. Methodology

## 3.1 Development Methodology

Figure 4 Waterfall Development Methodology [70]

The project will use a combination of Waterfall and Incremental development Methodologies. Using a blend of both approaches we will aim to utilise the advantages and minimise the disadvantages of both systems.

The Waterfall technique, as shown above, clearly outlines a methodical approach used in the development of a solution to record the switching on and off times of the streetlights in Pembrokeshire. Every project milestone is to be completed in sequence, which will ensure the project advances in order.

Advantages of Waterfall Methodology:

- Clear structure

- Easy to manage

- Early determination of goals

- Stable method

Disadvantages of Waterfall Methodology:

- Inflexible

- Delayed testing

## 3.2 Incremental Methodology

Figure 5  Increment Development Methodology [71]

Incremental development will help each "Waterfall" milestone to be broken down further. Every milestone will then follow the same procedures—requirement, design, implementation, and testing. This will mean that at every stage of the design the starting point is basic, with more layers adding improvements once the previous has been validated and tested.

Advantages of Incremental Methodology:

- Easy breakdown of tasks.

- Lowers delivery cost.

- Removes errors easily.

- Good system to use when using new Technology.

- Generates working prototypes quickly.

Disadvantages of Incremental Methodology:

- It requires a good planning designing.

- It is costlier than waterfall model.

- Difficulty in tracking progress, especially if multiple increments being developed simultaneously.

- More time spent on testing, can delay the project’s completion.

## 3.3 Software

3.3.1 Embedded C - will be used to build the software system of a PIC microcontroller, that will track and record data when a light has changed state between on and off. The software will also gather GPS information, ensuring that the data collected satisfies any auditing procedures recognising where and when the readings were taken. The microcontroller's programming will save the timestamp and GPS information to non-volatile memory.

3.3.2 Proteus - The Proteus software suite will be used to simulate the schematics before a prototype is produced. Working alongside the CCS compiler it will allow for an electronic simulation of the device, allowing for testing to be carried out before the build.

3.3.3 CCS Compiler - The CCS compiler tool will be used to compile the C code for the PIC Microcontroller. CCS was chosen as it has a user-friendly interface and is optimized for hardware features like I/O pins and peripherals. It will be used within Proteus for optimized build and debugging of the system.

## 3.4 Hardware

3.4.1 PIC Microcontroller - The PIC Microcontroller will be the heart of the monitoring device. Used to control the collection and processing of information from the attached peripherals.

3.4.2 Current Transformer - A CT clamped onto the conductor powering the luminaire will detect the change of current as the streetlight switches on and off.

3.4.3 GPS Chip - A GPS module will be added. This will ensure accurate data is logged to identify where data was collected. Not relying on the PIC to store the time will also safeguard against loss of power to the device and save programming onsite.

3.4.4 Various Electronic Components – Various items e.g.

- Resistors

- Capacitors

- LCD Screen

- Power Supply

- Voltage Regulator

- LEDs

- Diodes

- Op-Amps

## 3.5 Tools

3.5.1 PICkit 3 - A PICkit 3 programmer will be used to transfer the software to the PIC Microcontroller from the compiler software

3.5.2 Soldering Kit - Soldering of the components will be required to the PCB board

# 4. Design & Implementation

## 4.1 Design Specification

To verify that the PN switching of streetlights at PCC is being implemented correctly, a reliable light logging & monitoring system is required to log the switching on and off times of individual streetlights on an ad-hoc basis within the County. The device should be capable of being deployed quickly, with no modification needed to the device nor to the streetlights themselves. The design of the device should consider the different configurations of streetlight designs, as well as the diverse fixing and mounting systems within the PCC streetlighting portfolio. The design of the device will also consider the need to easily retrieve the data, to present it to members of the public. The data must be objective, to verify compliance with the councils PN policy, ensuring that cost savings are being achieved as planned, and any corporate complaints can be rejected.

The data needed to be collected from the device is as follows:

- Location of the logged information

- Time when the light is activated in the evening

- Time when the PN deactivates the light during the night

- Time when the PN activates the light in the morning

- Time when the light deactivates in the morning

- Power supply status

## 4.2 Output Requirements

To achieve the design specification, the Light Monitoring Device (LMD) must be powered by an independent power supply, be portable and adaptable. This is to ensure it will continue monitoring even when the site is remote and unpowered.

The LMD will need to be capable of not only connecting to a sensor but will need the capacity to store data during a potential 7-day testing cycle on non-volatile memory. A Green LED will need to be programmed to activate for 5 seconds to indicate that a switching has been logged and confirming successful data storage. Additionally, a Red LED should be on to indicate the LMD is switched on.

Environmental conditions will need to be considered during the design phase to ensure adequate Ingress Protection Ratings (also known as IP Rating) are met.

To debug the system and retrieve on/off events, real-time data must be presented on an LCD panel.

## 4.3 Existing Systems

Light monitoring and light logging devices are used for many purposes and in many key applications. They are used to continuously measure lighting levels and help us understand how much light is present in any given area. This measurement is crucial in many industries such as:

- Analysing Energy Usage – tracking light usage in buildings and outdoor spaces to help optimise energy consumption

- Lighting Management in BMS – Monitoring lighting levels in schools and other public buildings based on occupancy and lighting levels

- Plant Growth – controlling plant exposure to high light levels to optimize growth

- Food Safety – Monitoring food to ensure produce is optimally stored and shipped

- Ancient Artifact Preservation – Light overexposure can cause weakening, discoloration, yellowing and embrittlement. Damage caused by light exposure is both cumulative and irreversible [32]

- Industry & Work –By ensuring areas are well illuminated, workers reduce their likelihood of trips, slips and falls

Below is a detailed tabulated comparison of three existing systems that are on the market:

Table 1 Tabulated Comparison of Existing Systems [33], [34], [35]

## 4.4 Design Options

The design of the LMD must be adaptable to fit all the various streetlight types within PCC’s portfolio. These include:

- Traditional column design with lantern over carriageway

- Post top lantern

- Ornate/Decorative lantern and columns

- Wall mounted bracketed lanterns

Figure 6 PCC types of Streetlights: Traditional over carriageway, Post-Top, Decorative, Wall mounted

The choice of sensor to detect if the Streetlight is ON or OFF is critical to the success of this project. Choosing a sensor that is not compatible with one or more of the above streetlighting types will mean that the Design Specification is not met.

Table 2 Tabulated Comparison of Sensor Technology [36], [37], [38], [39]

The tabulated comparison above gives some explanation as to why the CT Clamp was chosen as the sensor for the LMD

## 4.5 The Design

### 4.5.1 Design Parameters

Table 2 below shows the parameters that the LMD will record and measure to satisfy the Design Specification.

Table 3 Parameters to Measure

### 4.5.2 Equipment Requirements

The equipment listed below will be required to construct the LMD:

- CT Clamp

- GPS Receiver

- GPS Antena

- DC-DC Converter

- PIC Microcontroller

- Non-Volatile Memory

- Power Supply

- LCD Screen

- Op Amp

- 5V Regulator

- LED Indicator Lights

- Buttons

- Various Electronic Components

- PCB

- Connectors

### 4.5.3 Current Transformer (CT Clamp) Selection

Table 4 Current Transformer Comparison [40], [41], [42]

Figure 7 Chosen Current Transformer - Carlo Gavazzi CTA5X100A5A (Datasheet - See Appendix D) [41]

Table 4 above compares three potential CT’s. The Panasonic was discarded as it had environmental limitations, while the Hobut was designed for multifunction meter use. Although expensive the Carlo Gavazzi fitted the requirement.

Below in Table 5 we see the comparison of the GPS modules, there is little difference between all three, however the Adafruit was chosen as the alternatives had slower delivery times.

### 4.5.4 GPS Selection

Table 5 GPS Receiver Comparison [43], [44], [45]

Figure 8 Chosen GPS Receiver - Adafruit 746 (Datasheet - See Appendix E) [43]

Additionally, the selected GPS receiver module will require an external active antenna. The chosen GPS antenna will give an additional 28 dB of gain and has a 5-meter-long cable. The antenna is magnetic so it will stick to the inside of a steel streetlighting column.

Figure 9 GPS Antenna (Datasheet - See Appendix F) [72]

### 4.5.5 DC-DC Converter Selection

Table 6 DC-DC Converter Comparison [46], [47], [48]

Figure 10 Chosen DC-DC Converter - RECOM RS3-0515D/H3 (Datasheet - See Appendix G) [48]

Table 6 above compares three potential DC-DC Converters. The TRACOPOWER was discarded as it was simply too expensive, while the RECOM Power model was selected over the XP Power as it has similar features but comes in a smaller package.

### 4.5.6 Memory Requirements

To store the data collected from the GPS receiver and the light switch on/off times via the CT, a calculation of the required Non-Volatile memory will be necessary. Non-Volatile memory is stored even when the device is powered down, as opposed to the Volatile memory which is erased once the device is powered down.

GPS Data - From Table 5 (GPS Receiver Comparison) the Adafruit 746 GPS module uses the industry standard NMEA-0183 frame format to represent the GPS location information. To understand the memory requirements, the NEMA output messages must be broken down.

Table 7 below shows the Output Messages from NEMA-0183 protocol.

Table 7 NMEA-0183 Output Messages

Since the LMD requires accurate time stamps to record the on/off times of the streetlight, location detail when it is switched on as well as fix indicator of the satellite signal to start recording, the device will utilise the GGA - Global Positioning System Fixed Data message from the GPS Module.

Table 8 contains the values of the following GGA example:

$GPGGA, 161229.487, 3723.2475, N, 12158.3416, W, 1, 07, 1.0, 9.0, M, , , ,0000*18

Table 8 GGA Data Format

To minimise the memory requirements, not all the message string is required to be stored on the device.

When the device is first switched on, it checks for the character below to be greater than 0. This will indicate a satellite fix.

$GPGGA, 161229.487, 3723.2475, N, 12158.3416, W, 1, 07, 1.0, 9.0, M, , , ,0000*18

Once the satellite fix has been established, the LMD will then capture and store the relevant Latitude and Longitude location information that is indicated below.

$GPGGA, 161229.487, 3723.2475, N, 12158.3416, W, 1, 07, 1.0, 9.0, M, , , ,0000*18

When the trigger value from the CT activates an interrupt within the PIC Microcontroller to capture a time stamp to record an ON or Off change in status of the streetlight, the LMD will then capture and store the time information as indicated below.

$GPGGA, 161229.487, 3723.2475, N, 12158.3416, W, 1, 07, 1.0, 9.0, M, , , ,0000*18

Table 9 Parameter Values

Table 9 above shows the number of characters that will be stored on the LMD memory. Each character value stored will require 1 byte of memory.

Table 10 No. of Bytes required for each write to memory

Table 11 Frequency of Measurement

Time Stamp Memory

6 𝐵𝑦𝑡𝑒𝑠 / ON or OFF ∗ 4 (𝐹𝑟𝑒𝑞𝑢𝑒𝑛𝑐𝑦 𝑜𝑓 write to memory / Day) = 24 𝐵𝑦𝑡𝑒𝑠 / Day

24 𝐵𝑦𝑡𝑒𝑠 / Day ∗ 7 (𝐷𝑎𝑦𝑠 𝑂𝑝𝑒𝑟𝑎𝑡𝑖𝑜𝑛) = 168 𝐵𝑦𝑡𝑒𝑠

Equation 1 Memory Required for 7-Day Logging

Table 12 Total Non-Volatile Memory required for 7 day Operation of Light Monitoring Device

### 4.5.7 Memory Selection

Tables 10, 11 and 12 above, tabulate the calculated minimum Non-Volatile memory required for the operation of our LMD for a 7-day monitoring period as per the Output Requirements of this report.

Although larger memory solutions are available, such as SD cards and USB flash drives, a built in EEPROM will offer ample storage for the relatively little memory requirements of the device.

Figure 11 Chosen EEPROM - Microchip 24LC1026 (Datasheet - See Appendix H) [73]

### 4.5.8 Microcontroller Selection

Table 13 Type of Output from Device

Table 13 above shows the type of output signal produced, that will be processed by the Microcontroller. The tabulated view below in Table 14 shows the minimum amount of Analog & Digital IO pins, Communication Devices and peripherals the Microcontroller will require. From this table of requirements for our Microcontroller, the filters can be set on the Microchip parametric part selector website tool to shortlist suitable Microcontrollers.

Table 14 Number of IO Pins required for PIC Microcontroller

With the above criteria used to filter Microchip products, 729 suitable PIC Microcontrollers were identified as suitable. 5 samples were chosen as a comparison in Table 15 below:

Table 15 PIC Microcontroller Comparison [49]

Figure 12 Chosen PIC Microcontroller - PIC16F887 - (Datasheet - See Appendix I) [74]

Figure 13 PIC16F887 Block Diagram [75]

### 4.5.9 Power Options

How the LMD is powered must be carefully assessed. The device must be portable and have enough energy to power the device for a minimum period of 7 days. There are many options available, these include:

- Battery

- Solar

- Mains Electric

Choosing the correct power source is essential for the device to meet the Design Specification.

Table 16 Tabulated Comparison of Power Sources [50], [51], [52]

The tabulated comparison in Table 16 above gives some explanation as to why Batteries were chosen as the power source of the LMD. Solar was rejected, as batteries would be needed as well as the solar system, and utilizing the utility power at the lamppost would be intrusive and would potentially require trained individuals to deploy the device.

### 4.5.10 Power Requirements

To calculate the power budget of an embedded device, you need to consider the power consumption of individual components and subsystems within that device. This is done by carefully studying the datasheets and obtaining the following information from them:

- Voltage

- Current Draw

This data can then be used to calculate power consumption using P = V × I for each component of the device. These are then totalled up for total power demand as shown in Table 17.

Table 17 Power Demand of Device

To estimate battery Capacity (mAh) the information from the datasheets is also used, but this time we need to consider how long each component is operational for while the device is switched on. As seen in Table 18 below

Table 18 Battery Capacity Requirements

### 4.5.11Power Selection

Table 19 Battery Comparison [53], [54], [55]

Figure 14 Chosen Battery – LiPo 10,000mAh - (Datasheet - See Appendix J) [55]

### 4.5.12 Battery Configuration

Figure 15 Battery Configuration

Figure 15 demonstrating the battery configuration using four 3.7V 10,000mAh LiPo batteries, arranged in a 2 Series, 2 Parallel arrangement to output 20,000mAh at 7.4V.

Series Connection

BAT 1 3.7v+3.7v BAT 2=7.4v

BAT 3 3.7v+3.7v BAT 4=7.4v

Series Connection

BAT 1,2 10,000mAh+10,000mAh BAT 3,4=20,000mAh

Equation 2 Battery Power Calculations

### 4.5.13 Miscellaneous Components

Table 20 Miscellaneous Components (#1)

Table 21 Miscellaneous Components (#2)

Table 22 Miscellaneous Components (#3)

## 4.6 Circuit Design

Figure 16 Power Supply Block Diagram

The Block diagram in Figure 16 shows the three different voltages required by the LMD. That is 7.4V, 3.3V and 5V. The diagram also shows what voltages are required for each peripheral device.

### 4.6.1 Power Rail Schematic

#### 4.6.1.1 Battery, Battery Metering & 7.4 Volt Supply

Figure 17 Power Supply Schematic - Battery, Battery Metering & 7.4V Supply

The schematic design in Figure 17 and Figures 18 & Figure 19 on the subsequent pages shows the step down from the 7.4 Volt Battery Power Supply to 5V via a 7805-voltage regulator, and from 5V to 3.3V via a 7833-voltage regulator. Note the presence of a Diode to protect against any back feed of voltage that may interfere with the battery voltage measurement, as well as the RED LED indicating that the LMD is switched on.

The Voltage Divider used to measure VBATT.

Vout=Vin*(R2/(R1+R2))

7.4V*(10kΩ10kΩ+10kΩ)=3.7V

Equation 3 Voltage Divider Calculations

#### 4.6.1.2 5 Volt Regulated Supply

Figure 18 Power Supply Schematic - 5V Regulated Supply

#### 4.6.1.3 3.3 Volt Regulated Supply

Figure 19 Power Supply Schematic - 3.3V Regulated Supply

### 4.6.2 DC-DC Converter Schematic

Figure 20 DC-DC Converter Schematic

The DC-DC Converter in Figure 20 powers the Operational Amplifiers used to Amplify and Rectify the voltage received from the CT.

### 4.6.3 PIC 16F667 Microcontroller Schematic

Figure 21 PIC16F887 Schematic

The schematic in Figure 21 shows the connection pins used on the PIC Microcontroller.

### 4.6.4 PIC Decoupler Schematic

Figure 22 showing how the decoupling capacitor is connected, its job is to supress high-frequency noise in power supply signals [65].

Figure 22 PIC Decoupling Capacitor

### 4.6.5 MCLR Schematic

The resistor and capacitor on the MCLR pin serve to provide a stable reset signal and prevent unintended resets. The resistor, typically 10K ohms, pulls the MCLR pin high when not actively driven low for reset. The capacitor, typically small 0.1μF, helps to maintain the reset state for a longer duration, preventing brief noise spikes from triggering a reset [66]. As seen in Figure 23.

Figure 23 Master Clear (MCLR) Schematic

### 4.6.6 CT Circuit, Amplifier & Rectifier Schematic

#### 4.6.6.1 CT Clamp & Simulated Switching of Streetlight Circuit

Figure 24 CT Circuit Schematic - Simulated Switching

The schematic design in Figure 24, and the following Figures 25, 26, 27 and Figure 28 all form part of the circuitry that converts the current read by the CT clamp that detects if the streetlight is in the On or Off state.

The schematic in Figure 24 is for the purpose of the Proteus simulation only. The switch and associated resistors simulate a 13-Watt Streetlight in the ON and OFF state.

VSINE = 230 Volts RMS

Streetlight = 13 Watt (when light is ON)

P/N Cell = 0.1 Watt (when light is OFF)

Light ON Resistor→  I=PV      13230=56.5 mA

R=VI      2300.056=4107Ω      R23=4107Ω

Light OFF Resistor→  I=PV      0.1230=0.434 mA

R=VI      2300.000434=529,954Ω      R24=529kΩ

Equation 4 Simulation of Light ON and OFF Calculations

#### 4.6.6.2 CT Burden Resistor

Figure 25 CT Circuit Schematic - Burden Resistor

The schematic in Figure 25 shows the burden resistor connected across the CT's secondary terminals. It acts as a load for the CT, creating a voltage drop that is proportional to the secondary current, this in turn reflects the primary current. This voltage is then measured by the Microcontroller to determine the primary current.

Streetlight = 56.5 mA (when light is ON)

CT Ratio = 0.05

Target Voltage = 0.5 Volts

RMS I→  Streetlight I*CT Ratio      0.056*0.05=2.8 mA RMS

Burden Resistor Value→  R=VI      Target VoltageRMS (I)     0.50.0028=178.6Ω

Nearest Resistor value=180Ω

RMS V→  V=I*R   k   0.0028*180=0.504 Volts RMS

Voltage Peak→  Voltage RMS*2      0.504*2=0.71 V

Equation 5 Burden Resistor Calculations

#### 4.6.6.3 Amplifier

Figure 26 CT Circuit Schematic - Amplifier

Figure 26 shows the first Op-Amp in the circuit. This is used as a non-inverting amplifier to amplify the voltage reading from the CT. Resistors R19 (Rf) and R20 (R1) are used to set the gain of the amplifier.

Rf = 900Ω	(R19)

R1 = 100Ω	(R20)

Gain=1+RfR1      1+900Ω100Ω=10Ω

Equation 6 Circuit Gain Calculation

#### 4.6.6.4 Rectifier

Figure 27 CT Circuit Schematic - Rectifier

The full-wave rectifier part of the circuit is shown in Figure 27 using a dual op-amp. This converts the amplified AC signal to a DC voltage. The first stage (U4:A) acts as a Half Wave Rectifier and outputs only the positive half-cycles of the input signal that flows through Diode 2, and the voltage appears at the junction of R3 and R4. During negative input cycles, the op-amp compensates to keep the output voltage at 0 by reversing bias on Diode 3. The second stage (U4:B) inverts and combines the input and rectified signals to reconstruct a full-wave signal. The result is a signal where both positive and inverted negative halves of the original waveform become positive.

#### 4.6.6.5 Filter

Figure 28 CT Circuit Schematic - Filter

Figure 28 above is a simple voltage regulation and filtering circuit using a Zener diode and a capacitor. The capacitor smooths out the voltage, while the Zenner diode regulates the voltage to 5V to protect the PIC Microcontroller.

### 4.6.7 GPS Schematic

Figure 29 GPS Schematic

The GPS module is connected to the PIC Microcontroller via UART (Universal Asynchronous Receiver/Transmitter) as shown in Figure 29.

### 4.6.8 LCD Display Schematic

LCD Schematic in Figure 30 showing connections to PIC Microcontroller.

Figure 30 LCD Display

### 4.6.9 EEPROM Schematic

Figure 31 EEPROM

EEPROM Schematic in Figure 31 showing connections to PIC Microcontroller via I2C.

### 4.6.10 Writing to EEPROM LED Schematic

Figure 32 Green LED Schematic

Figure 32 showing the Green LED that flashes when the EEPROM is written to.

R=Vs-VfIf

R=5V-2V8.5mA

R=3V8.5mA      R=353Ω

Nearest Resistor value=360Ω

Equation 7 LED Resistor Value Calculation

### 4.6.11 Button Assembly Schematic

Figure 33 Button Assembly Schematic

Button Assembly in Figure 33 shows connections to PIC Microcontroller.

### 4.6.13 Full Proteus Schematic

Figure 34 Full Proteus Schematic

The full diagram in Figure 34 shows the schematic used to create the simulation on the Proteus Software.

## 4.7 The Software

Figure 35 Flowchart of the software code

The block drawing in Figure 35 shows the complete software layout.

Figure 36 Code Extract 1 - Extracting Time from NEMA String

The extract of code in Figure 36 contains the interrupt routine that extracts and stores the UTC (Coordinated Universal Time) from the NEMA sentence that starts with the keyword “$GPGGA”.  Once the relevant time data is captured, the code then converts the ASCII-encoded characters into their corresponding decimal values.

Figure 37 Code Extract 2 - Test Screen Function

The extract of code in Figure 37 contains the Test Screen function, and shows how live data from the GPS, CT and Battery are displayed.

Figure 38 Code Extract 3 - The Menu

The extract of code in Figure 38 shows how the Menu Display is coded along with how the code executes functions based on the selected menu option.

Figure 39 Code Extract 5 - Clearing the EEPROM Memory

The code in Figure 39 controls the clearing of the EEPROM memory when the DELETE button is pressed.

Figure 40 Code Extract 4 - Change of State Time Capture

The code in Figure 40 detects when current crosses the threshold of 10, either above or below, which indicates if a light is turned ON or OFF and stores the time of the event in the EEPROM, along with the event flag 0 (OFF) or 1 (ON). The Green LED also provides a visual confirmation by flashing for 1.5 seconds.

A full copy of the C Code can be found in Appendix R of this report.

## 4.8 Cost and Figures

Table 23 Prototype Bill-of -Quantities

# 5. Evaluation & Results

This project set out with the aim of designing and developing a light monitoring device to log the switching ON and OFF times of streetlights in Pembrokeshire to answer the question of “does this streetlight comply with PN switching policy?” The core objectives were to detect when a light comes ON and OFF, logging the corresponding times and storing this data for later retrieval using a PIC Microcontroller. This evaluation will give an overview of the project’s outcomes by examining the results obtained in testing and suggests improvements for further development of the device.

## 5.1 Design and Implementation Overview

The system design includes:

- A CT clamp to detect current and sense ON/OFF states of the light.

- A PIC16F877 microcontroller programmed in C using the CCS compiler.

- GPS module to provide real-time timestamps.

- LCD to display system status and logged events.

- Buttons for menu navigation (MOVE, SELECT, BACK, DELETE).

- External EEPROM for data storage.

- LED indicator to confirm successful EEPROM writes.

Figure 41 LMD System Block Diagram

The Block diagram in Figure 41 shows the LMD architecture and how they are connected and communicate with each other.

## 5.2 Evaluation of the Objectives

Evaluating the objectives will provide a clear benchmark for measuring the overall success of the project [67].

## 5.2.1 Objective 1: Design and develop a compact, cost-effective monitoring device using a PIC microcontroller

A functioning breadboard prototype was designed and assembled using a PIC Microcontroller and various easily sourced off the shelf components as shown in Figure 42. The hardware was compact, cost-effective and the use of Lithium Polymer batteries makes the device portable and allows for untethered operation. The Objective was achieved in principle; however, the device would be far more compact if it was packaged within a PCB board and enclosure.

Figure 42 Full Breadboard Prototype

## 5.2.2 Objective 2: Detect switching ON & OFF events

This Objective was achieved in full. Both the Proteus simulations and physical testing demonstrated that the device could accurately detect changes in current to indicate if the light was switching ON or OFF. Multiple tests using simulated and physical prototype confirmed that the CT and associated amplification circuitry produce a clear voltage signal which was then interpreted by the PIC Microcontroller to correctly detected state changes.

Figure 43 Graphical Expression of how CT Signal is Amplified and Rectified

Figure 42 demonstrates how the voltage signal changes as it travels along the amplification and rectification circuit. The green waveform represents the sine wave from the CT before it is amplified. The red waveform is the amplified signal, while the blue waveform represents the half wave rectified signal, and the yellow waveform is the rectified and filtered version of the red sine wave that is fed into the PIC Microcontroller to read if the current is HIGH (ON) or LOW (OFF).

## 5.2.3 Objective 3: Capture GPS time at switching events

Figure 44 Proteus Light ON and OFF Times

While the Proteus simulation for GPS time extraction was implemented and proven in simulation as seen in Figure 44, the GPS module failed to acquire a fix during indoor testing. This is likely to be due to a lack of adequate satellite signal preventing accurate timestamp capture during the physical test. The Objective was partially achieved; however, an outdoor test would likely have resulted in achieving a positive result for this objective. An outdoor test was planned, however time constraints meant this was not possible.

The characters 1 & 0 located at the end of the timestamp on the LCD screen denotes the event, and if the light was ON or OFF during this time-period. This is visually represented on the graph in Figure 45.

Figure 45 Light ON and OFF Graph

## 5.2.4 Objective 4: Log data to external EEPROM

Although the hardware was installed to the breadboard prototype as seen with red circle in Figure 46 for external EEPROM storage, the software did not have this included in the code. Time constraints prevented the coding of I2C to PIC interfacing. The internal PIC EEPROM however was utilized within the code, and both the Proteus simulation and the physical test successfully stored the captured data to the internal EEPROM. This objective has partially been met, as the EEPROM code structure is in place, however the software limitation can be corrected relatively easily with more time.

Figure 46 Location of EEPROM on Breadboard

## 5.2.5 Objective 5: Providing real-time feedback via LCD and LED indicators

The 20x4 LCD was tested to display some opening credits and to display a menu interface. Menu functionality proved successful in both simulation and physical testing. Input from the four buttons proved successful, allowing the user to navigate between different displays. As well as having the function of deleting stored data on the internal EEPROM, the menu test screen function also displayed the Battery Voltage, the CT voltage reading and the time captured from the GPS, however this was not displayed during the physical test.

The Green EEPROM write indicator LED responded as expected during both tests, flashing for 1.5 seconds following a successful log of event. The RED LED power indicator also illuminated as expected. All this meant the objective was met successfully.

## 5.2.6 Objective 6: Enable retrieval of logged data for analysis and feedback

The Proteus simulation was successful in nearly all objectives. However, the software was only coded to record four events (i.e., four ON/OFF changes), which would represent a single day’s data logging. The objective was to monitor over a full week period, making this a limiting factor in the testing procedure. Due to the absence of a data retrieval interface, this final stage remains incomplete. However, it is entirely within reach if the external EEPROM interface is fixed, and a simple serial terminal or SD card is used to extract data from memory.

| Have objectives been met? |  |
| --- | --- |
| Objective | Met? |
| Design and develop a compact, cost-effective monitoring device using a PIC microcontroller | Partially |
| Detect switching ON & OFF events | Yes |
| Capture GPS time at switching events | Partially |
| Log data to external EEPROM | Partially |
| Providing real-time feedback via LCD and LED indicators | Yes |
| Enable retrieval of logged data for analysis and feedback | No |

Table 24 Evaluation of Objectives

Figure 47 Location of GPS Module on Breadboard

Overall, the project has partially achieved its objectives. Proving the concept that streetlight ON and OFF states and switching times can be detected by sensing the change in the current, which is the basis of the LMD. The software that was developed to manage the detection of events was simplistic in its functionality, and was generally easy to operate, however the LMD did prove to encounter some minor glitches during testing. Further software testing and debugging sessions needs to be carried out to establish if they are the result of memory difficulties, coding logic failings, or hardware-related issues such as button debounce.  Despite this, the software glitches did not prevent the demonstration of basic system operation.

The failure to capture the GPS time in the physical test is a significant cause for concern; nonetheless, it is more likely to be attributed to the testing environment rather than flaws in the design. The Proteus simulation demonstrates that it is possible to handle the GPS data, Figure 47 shows that the hardware is connected to the system correctly, which emphasises that the issue is likely to be pointed towards physical issues and not towards hardware or software faults.

The inability to add external EEPROM logging is not a failure, but merely a wasted opportunity to strengthen the results from testing the device. It does not undermine the project; it only limits the scope for recording multiple ON & OFF events. The PIC microcontroller’s built-in EEPROM proves that the code’s design is correct, as it successfully stores switching data in testing. With a minor software modification, adding a I²C interface, a much larger external memory could be integrated, significantly enhancing the LMD’s data logging and testing capabilities. The hardware is already in place as seen in Figure 45.

The integration of a user-friendly interface that is comprised of buttons and an LCD display means that in terms of interaction and usability the system can browse through menu selections and present appropriate data.

On both the circuit and schematic levels, all the hardware sub-systems, including the power supply, CT detection, signal conditioning, GPS receiver, LCD interface, EEPROM, and user input, are properly integrated.

The results from testing are relatively what was expected of a first working prototype. The CT circuit behaved as expected and with results similar to the simulation results, and the GPS failure to acquire a fix indoors should have been anticipated. The minor software and hardware glitches are also not uncommon in early prototypes, and with further testing these should be debugged.

# 6. Conclusions and Recommendations

This project started by asking one key question, “does this streetlight comply with PCC’s PN switching policy?”. This needed to be answered due to the number of corporate complaints received by the authority in recent years and the lack of systems on the market in place to verify and answer the problem. The aim therefore was to design and develop a device that could be used across the PCC streetlighting network to log the switching ON and OFF times.

The research and literature review highlighted the advantages both in terms of ecological and economical value of reduced illumination of streetlights via the PN system but also showed that incorrect application of this can cause residents to have numerous concerns. Therefore, the device needed to be both robust and accurate to give precise feedback to members of the public.

A design specification was drawn up to decide what data was needed to be collected from the LMD, along with the output requirements needed to achieve the design specification. Existing systems were investigated, but no devices were found that were designed specifically for streetlights, and all the existing devices were predominantly designed for indoor use. The types of streetlights currently used within PCC’s streetlighting portfolio was investigated prior to looking at sensor technology for the LMD. The sensor used would need to be compatible with the four main types of lanterns used within the county.

Possible sensor technology was compared with advantages and disadvantages of each discussed, before settling on Current Transformer technology. This was chosen due to having unintrusive properties as well as the lack of a mobile platform needed to install such sensors. Further research then led to decisions being made on the other components needed to develop the LMD. GPS Module, DC-DC Converter, Voltage Regulators, Operational Amplifiers, LEDs and LCD Display. Memory requirements were heavily researched, where a good understanding of how GPS receivers receive data was needed to calculate the required memory for storing seven days of data. This research also proved highly valuable during the coding procedure and the writing of the software that captured the UTC time from the GPS module. The requirements were relatively small, so a decision was made to use an external EEPROM as non-volatile memory. Microcontrollers were then compared, and the PIC16F887 was chosen as it had all the Input and Output ports required for the design.

One of the main objectives for the device was that it should be “easily” installed on the existing streetlighting network. This meant that choosing the correct power option for the device was going to be critical. Battery, Solar and Hard-wire options were all looked at, but due to its mobility and unintrusive nature, the battery was decided upon.  The battery power requirement and capacity then needed to be calculated to ensure the device logged data for the full seven-day monitoring period.  Various battery options were researched from D Cell Alkaline to USB Power Banks, but a Lithium Polymer battery solution was decided on as they are lightweight and have lower self-discharge rate. As the majority of LiPo batteries come in 3.7volt packages, it meant that several would be required in a 2 Series, 2 Parallel arrangement.

Figure 48 Proteus Schematic

The circuit design of the LMD proved to be complex in some areas and straight forward in others. The power rails were straight forward with two voltage regulators stepping down the voltage from 7.4volts to 5volts and then to 3.3volts. A voltage divider was placed near the battery which fed back a battery voltage reading to the Microcontroller, while a Red LED was placed parallel to the 5volt supply to indicate that the device is powered on. A scattering of capacitors was added to smooth out fluctuations. PIC decouplers were added to the Microcontroller as per datasheet, as well as capacitor and resistor to the MCLR pin. The GPS module was connected to the PIC via UART and to the 5volt power rail. The external EEPROM was connected to the PIC via I2C and to the 5volt power rail. The Green LED indicator light that flashed when the switching event was stored to the EEPROM was connected to pin A7 of the Microcontroller, and the buttons to pins A0, A1, A2 & A3 respectively. The LCD Screen was connected to the 3.3volt power rail and to pins D0, D1, D2, D3, D4, D5 & D6. The complex part of the circuitry is the current transformer to the Microcontroller. The CT outputs the secondary current from the transformer and the burden resistor then converts that current into a measurable voltage that is in proportion to the current flowing through the conductor in the primary circuit. That voltage is then amplified through the first Op-Amp before being rectified through the second Op-Amp, before having the signal smoothed out via a low pass filter. A full schematic was designed in the Proteus software as seen in Figure 48.

The CCS Compiler was then used to write the code. Challenges included understanding which NEMA output string was required from the GPS, which characters to extract, storing the data, and then converting it into integers to be displayed on the LCD Display and storing them on the PIC EEPROM. The software was then uploaded to the Microcontroller via a PICkit 3, using In-Circuit Serial Programming (ICSP) and the MPLAB IPE Software.

Figure 49 Programming the PIC Microcontroller

These recommendations for further development would mean the LMD has met its objectives in full, and would add more functionality to the design:

- Interfacing external EEPROM via I2C – The hardware is already n place here for external memory storage. Additional time on coding will allow the LMD to capture data and store on the EEPROM

- Extend memory to minimum 28 logged entries – Once the external memory has been interfaced, then 7-day logging can occur. Some software tweaks would be necessary to handle the data once stored.

- Capturing location data – A small software tweak is recommended here. This would follow a similar code to the retrieval of the UTC time and give further credibility to the results captured.

- Outdoor testing – This will help to validate the GPS design. GPS modules require line-of-sight to satellites which indoor testing can prevent, especially with concrete or metal shielding. These can block or weaken signals.

- PCB design – The next evolution of the design process would be to transfer the breadboard prototype to a compact PCB once the hardware has been debugged.

- Enclosure Design – The LSD enclosure will need to be durable to protect from damage, with a sufficient IP to protect the components from water and dust. Some ventilation will be required for heat dissipation and easy access will be essential. A 3D printed enclosure is proposed, made either from ABS (Acrylonitrile-Butadiene-Styrene) due to its high impact resistance, or PETG (Polyethylene-Terephthalate-Glycol) as it has a strong water and moisture barrier as well as good impact resistance, however this might not be a suitable option due to it being slightly flexible [68].

- Develop data retrieval (SD Card or serial interface via USB) – This would give the LMD a boost in functionality in everyday use as exported logs, either in excel or .txt format can easily be graphed to perform time analysis and reporting to members of the public.

- Real time reading via IoT or Wi-Fi – Adding this functionality would greatly increase the scope for this device. Viewing ON and OFF events from anywhere, as well as triggering email or SMS notifications would easily be achieved. The real advantage of this would be to monitor energy usage and potentially reduce bills by more accurately reporting the amount of time the streetlight is illuminated.

During the testing and evaluation procedure, it was found that the project did have some shortcomings, and only partially achieved its objectives. There was some small software glitches encountered, but despite these issues it did not prevent the demonstration of basic system operation and functionality. In conclusion the concept and theory behind the design was proved, with minor software tweaks and a little more time a full working model could be produced.

# 7. Reflection

Reflecting on my experience of undertaking this project, I can say without hesitation that it has been one of the most demanding, informative, and transformative experience I have ever undertaken. It tested not only my technical knowledge but also my personal resilience, organisation skills, and determination. As one of the largest individual projects I’ve ever carried out, it challenged me on many fronts, and I’ve come away from it with a much better understanding of myself and the profession I am working in.

At the core of this project was a technical challenge; design a system using a PIC Microcontroller to monitor streetlight activity and verify that PCC’s PN switching policy was being correctly implemented. While the concept seemed straightforward, detect current changes at lights turned ON and OFF, capture the timestamp via GPS, store and display the data. Bringing all these elements together in a single functioning system was much more difficult in practice.

However, the technical issues were only part of my story. What made this project particularly difficult was trying to balance it alongside full-time work, family responsibilities, and some minor health issues. Juggling these demands meant I often had to work late into the night and give up weekends. I missed social activities, special family occasions, and valuable downtime to ensure I met the project targets. There were points where fatigue, stress, and frustration nearly got the better of me. And yet, looking back now, those sacrifices were certainly worthwhile. I developed strong time management skills; planning each week carefully, trying to set achievable goals, and then constantly adjusting the plan when things didn’t go as expected. Learning how to keep moving forward, even when time was short, motivation was low or things going wrong, is a lesson I know will serve me well throughout my career at PCC.

The project also helped me to bring together concepts learned in various modules learned along the way. This project would not have been possible without the hard work put in during the previous 5 years not only in the BEng course, but also HND and HNC beforehand. Modules like Electrical and Electronic Principles, Micros Peripherals and Interfaces, Electronic Systems Design and Electronics 2 helped to connect theory to real time application. University lectures often explained concepts as in textbooks, as ideal inputs, clean outputs and perfect conditions. Reality as I found is a little different. I had to deal with noise, environmental circumstances and hardware limits. Learning how to work with these, rather than trying to eliminate them entirely, was one of the most challenging parts of the experience.

Technically, the steepest learning curve was the programming aspect of the project. Having no previous experience in embedded C and the CCS compiler software, I put this aspect of the project off for as long as possible due to fear of failure. My initial approach was to look at the whole program in its entirety, which quickly led to stress and frustration as the code made no sense whatsoever. I soon realised after speaking to the supervisor and other engineers within the industry of the benefits of breaking the code down into the different functions that needed to be achieved and then breaking them down into their smaller structures. This along with writing down on paper what I was trying to achieve (a skill that helped in coding Wallace Tree and Brauns Multipliers earlier in the course) meant it started making sense. This aspect of the project pushed me well beyond my comfort zone and improved my skills to the point where I have advanced my basic programming skills and now look forward to the prospect of continuing this after my academic studies have finished.

The project taught me a huge amount not only about Electronics but also about myself. It forced me to grow into the role of a problem-solver and, at times, a project manager. Some of the most valuable professional skills I have developed are the ability to create clear, concise and accurate written materials for various purposes, including reports, technical documentation and communication with elected officials. A skill that will serve me well while progressing my career through the authority. Communication also played a big part. Although the work was done independently, I frequently had to explain problems and progress to my supervisor during weekly meetings, listen to feedback, and apply suggestions to improve the outcome. The presentations required as part of the project have also enhanced my speaking skills, and I now find carrying out presentations in meetings with colleagues far less daunting.

One of the most exciting outcomes of the project was the interest shown recently by a certain professional in the streetlighting industry, with whom I discussed the concept of my design during a meeting after he asked how my degree was coming along. They saw the value in a simple device that could help local councils or contractors verify part-night switching and improve energy efficiency monitoring. This kind of industry validation was incredibly motivating and confirmed that the project has real-world potential beyond the university environment. Knowing that people in the sector are genuinely interested may in the future open the door to future collaboration, which could play a key part in both my career and the long-term evolution of the LMD.

In summary, this project ended up being far more than just a university module. It was an experience that helped me develop as an individual and as professional. I developed a working model of the LMD that while not without flaws, did absolutely demonstrate and prove the concept of my design. I expanded my technical knowledge of Electronics, gained experience and skills in programming and learned problem solving skills. At the same time, managing full-time work, family life, and personal challenges, often at the cost of rest and social time. I will take the lessons I’ve learned from this project into my work as a streetlighting engineer, potentially helping me project manage schemes better, and to develop smarter and more efficient systems of work. And with genuine industry interest in my concept, I’m hopeful that this project isn’t just a degree project, but the beginning of something bigger.

# References

[1]	A. T. Murray and X. Feng, ‘Public street lighting service standard assessment and achievement’, Socioecon Plann Sci, vol. 53, pp. 14–22, Mar. 2016, doi: 10.1016/J.SEPS.2015.12.001.

[2]	J. Green, C. Perkins, R. Steinbach, and P. Edwards, ‘Reduced street lighting at night and health: A rapid appraisal of public views in England and Wales’, Health Place, vol. 34, pp. 171–180, Jul. 2015, doi: 10.1016/j.healthplace.2015.05.011.

[3]	M. Pagden, K. Ngahane, and M. S. R. Amin, ‘Changing the colour of night on urban streets - LED vs. part-night lighting system’, Socioecon Plann Sci, vol. 69, p. 100692, Mar. 2020, doi: 10.1016/J.SEPS.2019.02.007.

[4]	G. Al-Haji, ‘The Impact of New Street Lighting Technologies on Traffic Safety’, Journal of Traffic and Logistics Engineering, vol. 2, no. 3, 2014, doi: 10.12720/jtle.2.3.202-205.

[5]	T. Ściężor, ‘Effect of street lighting on the urban and rural night-time radiance and the brightness of the night sky’, Remote Sens (Basel), vol. 13, no. 9, May 2021, doi: 10.3390/rs13091654.

[6]	L. Tompson et al., ‘Absence of Street Lighting May Prevent Vehicle Crime, but Spatial and Temporal Displacement Remains a Concern’, J Quant Criminol, vol. 39, no. 3, pp. 603–623, Sep. 2023, doi: 10.1007/s10940-022-09539-8.

[7]	M. W. Davies and D. P. Farrington, ‘An examination of the effects on crime of switching off street lighting’, Criminology and Criminal Justice, vol. 20, no. 3, pp. 339–357, Jul. 2020, doi: 10.1177/1748895818818861.

[8]	C. Perkins et al., ‘What is the effect of reduced street lighting on crime and road traffic injuries at night? A mixed-methods study’, Public Health Research, vol. 3, no. 11, pp. 1–108, Sep. 2015, doi: 10.3310/phr03110.

[9]	M. Asif, S. Shams, S. Hussain, J. A. Bhatti, M. Rashid, and M. Zeeshan-ul-Haque, ‘Adaptive Control of Streetlights Using Deep Learning for the Optimization of Energy Consumption during Late Hours’, Energies (Basel), vol. 15, no. 17, Sep. 2022, doi: 10.3390/en15176337.

[10]	‘Carbon footprint - Streetlighting - Pembrokeshire County Council’. Accessed: Feb. 03, 2025. [Online]. Available: https://www.pembrokeshire.gov.uk/our-action-plan/carbon-footprint-streetlighting

[11]	G. Rider, ‘The pros and cons of different approaches to LED street lighting’. [Online]. Available: https://www.researchgate.net/publication/368771305

[12]	P. M. Cozens, R. H. Neale, J. Whitaker, D. Hillier, and M. Graham, ‘Crime Prevention and Community Safety: An International Journal A Critical Review of Street Lighting, Crime and Fear of Crime in the British City’, 2003.

[13]	R. Steinbach, C. Perkins, and L. Tompson, ‘The effect of reduced street lighting on road casualties and crime in England and Wales: controlled interrupted time series analysis’, J Epidemiol Community Health, vol. 69, pp. 1118–1124, 2015, doi: 10.1136/jech.

[14]	G. G. Thiel, S. R. Ensslin, and L. Ensslin, ‘Street lighting management and performance evaluation: Opportunities and challenges’, Lex Localis, vol. 15, no. 2, pp. 303–328, 2017, doi: 10.4335/15.2.303-328(2017).

[15]	T. Mayat, ‘The role of governance in assessing satisfaction with local highways in England’.

[16]	M. Kopczynski and M. Lombardo, ‘Comparative Performance Measurement: Insights and Lessons Learned from a Consortium Effort’.

[17]	‘Performance benchmarking - apse’. Accessed: Feb. 03, 2025. [Online]. Available: https://apse.org.uk/index.cfm/apse/performance-networks/information-hub/why-join-performance-networks/performance-benchmarking/

[18]	M. Y. Mukta, M. A. Rahman, A. T. Asyhari, and M. Z. Alam Bhuiyan, ‘IoT for energy efficient green highway lighting systems: Challenges and issues’, May 15, 2020, Academic Press. doi: 10.1016/j.jnca.2020.102575.

[19]	‘The illuminating history of lighting | English Heritage’. Accessed: Feb. 04, 2025. [Online]. Available: https://www.english-heritage.org.uk/visit/inspire-me/blog/blog-posts/history-of-lighting/

[20]	‘Ekobase Global Inc. | Street lighting technology comparison’. Accessed: Feb. 04, 2025. [Online]. Available: https://www.ekobaseglobal.com/index.php/en/learning-center/street-lighting-technology-comparison

[21]	S. Khemakhem and L. Krichen, ‘A comprehensive survey on an IoT-based smart public street lighting system application for smart cities’, Franklin Open, vol. 8, p. 100142, Sep. 2024, doi: 10.1016/j.fraope.2024.100142.

[22]	M. Mahoor, Z. S. Hosseini, A. Khodaei, A. Paaso, and D. Kushner, ‘State-of-the-art in smart streetlight systems: a review’, Mar. 01, 2020, John Wiley and Sons Inc. doi: 10.1049/iet-smc.2019.0029.

[23]	G. Gagliardi et al., ‘Advanced adaptive street lighting systems for smart cities’, Smart Cities, vol. 3, no. 4, pp. 1495–1512, Dec. 2020, doi: 10.3390/smartcities3040071.

[24]	P. Yadav, ‘Smart Street Lighting System’, doi: 10.13140/RG.2.2.32106.75200.

[25]	E. Dizon and B. Pranggono, ‘Smart streetlights in Smart City: a case study of Sheffield’, J Ambient Intell Humaniz Comput, vol. 13, no. 4, pp. 2045–2060, Apr. 2022, doi: 10.1007/s12652-021-02970-y.

[26]	R. Shaw, ‘Streetlighting in england and wales: New technologies and uncertainty in the assemblage of streetlighting infrastructure’, Environ Plan A, vol. 46, no. 9, pp. 2228–2242, 2014, doi: 10.1068/a130313p.

[27]	‘Central Management Systems - Elexon BSC’. Accessed: Feb. 08, 2025. [Online]. Available: https://www.elexon.co.uk/operational/unmetered-supplies/central-management-systems/

[28]	G. W. Denardin, C. H. Barriquello, A. Campos, R. A. Pinto, M. A. Dalla Costa, and R. N. Do Prado, ‘Control Network for Modern Street Lighting Systems’.

[29]	A. Omar et al., ‘Smart City: Recent Advances in Intelligent Street Lighting Systems Based on IoT’, 2022, Hindawi Limited. doi: 10.1155/2022/5249187.

[30]	C. Skandali, N. Papatzelakis, and L. T. Doulos, ‘The Role of Adaptive Lighting in Street Lighting Applications’.

[31]	F. Agramelal, M. Sadik, Y. Moubarak, and S. Abouzahir, ‘Smart Street Light Control: A Review on Methods, Innovations, and Extended Applications’, Nov. 01, 2023, Multidisciplinary Digital Publishing Institute (MDPI). doi: 10.3390/en16217415.

[32]	‘Light Exposure for Artifacts on Exhibition | Conservation Center for Art & Historic Artifacts’. Accessed: Mar. 01, 2025. [Online]. Available: https://ccaha.org/resources/light-exposure-artifacts-exhibition

[33]	‘HOBO UX90-002M Light on/off Data Logger (512K) | Tempcon Instrumentation’. Accessed: Mar. 01, 2025. [Online]. Available: https://www.tempcon.co.uk/hobo-ux90-light-on-off-data-logger-ux90-002m

[34]	‘P01157167 CHAUVIN ARNOUX, Data Logger, PEL52, Energy, Power, 2 Channel, Current, Voltage, Bluetooth & WiFi, USB, LCD | Farnell® UK’. Accessed: Mar. 09, 2025. [Online]. Available: https://uk.farnell.com/chauvin-arnoux/p01157167/data-logger-energy-power-2-channel/dp/4136467?CMP=KNC-GUK-GEN-KWL-RLSA-PUR-TEST-921&mckv=_dc|pcrid|610187768070|&gad_source=1&gclid=Cj0KCQiAlbW-BhCMARIsADnwasou10ZVqvSdwgY_k6sEw4SwnH7X3K802UVTaZrPtVaeT1Vkzbst76oaAktyEALw_wcB

[35]	‘Multi Use GPS 4G Temperature And Light Data Logger (Cloud Based) - Klipspringer’. Accessed: Mar. 01, 2025. [Online]. Available: https://portal.klipspringer.com/products/multi-use-gps-4g-temperature-and-light-data-logger-lc50000.html?filter_set[]=238,145,160,1106

[36]	‘Advantages and Disadvantages of Thermopile sensor’. Accessed: Mar. 09, 2025. [Online]. Available: https://www.rfwireless-world.com/Terminology/Advantages-and-disadvantages-of-Thermopile-Sensor.html

[37]	T. Connectivity, ‘THERMOPILE SENSOR FOR CONTACTLESS TEMPERATURE APPLICATION NOTE’.

[38]	‘LDR - Advantages and Disadvantages (Limitations)’. Accessed: Mar. 09, 2025. [Online]. Available: https://www.electronicsforu.com/technology-trends/learn-electronics/ldr-advantages-disadvantages#limited-sensing-capabilities

[39]	‘What Are Advantages and Disadvantages of Current Transformer? - Blue Jay’. Accessed: Mar. 09, 2025. [Online]. Available: https://cqbluejay.com/what-are-advantages-and-disadvantages-of-current-transformer/

[40]	‘AKW4802B PANASONIC, Current Transformer, Clamp-On, Split Core, 3000:1 | Farnell® UK’. Accessed: Mar. 02, 2025. [Online]. Available: https://uk.farnell.com/panasonic/akw4802b/current-transformer-3000-1/dp/3954124

[41]	‘CTA5X100A5A CARLO GAVAZZI, Current Transformer, Split Core, 100:5, Class 3, 23.9 mm, 50Hz / 60Hz | Farnell® UK’. Accessed: Mar. 02, 2025. [Online]. Available: https://uk.farnell.com/carlo-gavazzi/cta5x100a5a/current-transformer-100a-50hz/dp/4558731

[42]	‘CTSCMWH30/0.333V | HOBUT CTSCM Series Split Core Current Transformer, 30A Input, 333 mV Output, 10mm Bore | RS’. Accessed: Mar. 02, 2025. [Online]. Available: https://uk.rs-online.com/web/p/current-transformers/9145290?gb=a

[43]	‘746 Adafruit | Mouser United Kingdom’. Accessed: Mar. 02, 2025. [Online]. Available: https://www.mouser.co.uk/ProductDetail/Adafruit/746?qs=GURawfaeGuDgnSNeg1CIag%3D%3D

[44]	‘TEL0132 DFROBOT, GPS Receiver Module, 2.7 V to 3.6 V, 12-CH, 2.5 m | Farnell® UK’. Accessed: Mar. 02, 2025. [Online]. Available: https://uk.farnell.com/dfrobot/tel0132/gps-2-7v-3-6v-12-ch-2-5m-i2c/dp/3769990?gross_price=true&CMP=KNC-GUK-GEN-SHOPPING-PLA&gad_source=1&gclid=Cj0KCQiA4-y8BhC3ARIsAHmjC_EtApops0j_qMxcfcu9DMpKnwTNZySkYrdBq61TLA4N56f39iM49-caAtXvEALw_wcB

[45]	‘GPS-19166 SparkFun | Mouser United Kingdom’. Accessed: Mar. 02, 2025. [Online]. Available: https://www.mouser.co.uk/ProductDetail/SparkFun/GPS-19166?qs=9vOqFld9vZXktyKL7v5pog%3D%3D

[46]	‘TEL 3-1223 | TRACOPOWER TEL 3 DC-DC Converter, ±15V dc/ ±100mA Output, 9 → 18 V dc Input, 3W, Through Hole, +85°C Max Temp | RS’. Accessed: Mar. 02, 2025. [Online]. Available: https://uk.rs-online.com/web/p/dc-dc-converters/3965174P?searchId=3fa8e451-6168-48d9-bb5a-81d75cfc7df9&gb=s

[47]	‘JCA0205D03 XP Power | Mouser United Kingdom’. Accessed: Mar. 02, 2025. [Online]. Available: https://www.mouser.co.uk/ProductDetail/XP-Power/JCA0205D03?qs=w%2Fv1CP2dgqq0HL2U5itnxQ%3D%3D

[48]	‘RS3-0515D/H3 RECOM Power | Mouser United Kingdom’. Accessed: Mar. 02, 2025. [Online]. Available: https://www.mouser.co.uk/ProductDetail/RECOM-Power/RS3-0515D-H3?qs=8OBu2JtKQqpPz4i1qmzULQ%3D%3D

[49]	‘8-bit PIC MCU Products Parametric Search’. Accessed: Mar. 02, 2025. [Online]. Available: https://www.microchip.com/en-us/parametric-search.html/717?filters=JTdCJTIyYWN0aXZlU2xpZGVyRmlsdGVycyUyMiUzQSU1QiU1QiUyMlNQSSUyMiUyQyU1QjIlMkMxJTVEJTVEJTVEJTJDJTIyYWN0aXZlTXVsdGlzZWxlY3RGaWx0ZXJzJTIyJTNBJTVCJTIySTJDJTNBMSUyMiU1RCUyQyUyMmNhdGVnb3J5ZHJvcGRvd24lMjIlM0ElNUIlMjJNaWNyb2NvbnRyb2xsZXJzJTIwYW5kJTIwTWljcm9wcm9jZXNzb3JzJTIyJTJDJTIyOCUyMC0lMjBiaXQlMjBNaWNyb2NvbnRyb2xsZXJzJTIyJTJDJTIyOC1iaXQlMjBQSUMlMjBNQ1UlMjIlNUQlN0Q=

[50]	‘Advantages and Disadvantages of Embedded Battery Chargers’. Accessed: Mar. 16, 2025. [Online]. Available: https://blog.epectec.com/advantages-and-disadvantages-of-embedded-battery-chargers

[51]	‘17 Advantages & Disadvantages of Solar Energy (March 2025)’. Accessed: Mar. 16, 2025. [Online]. Available: https://www.greenmatch.co.uk/solar-energy/pros-and-cons

[52]	‘Designing Low-Power Embedded Systems | Krasamo’. Accessed: Mar. 16, 2025. [Online]. Available: https://www.krasamo.com/low-power-embedded-systems/

[53]	‘Industrial D Alkaline Batteries, 12 Pack - Energizer | CPC’. Accessed: Mar. 16, 2025. [Online]. Available: https://cpc.farnell.com/energizer/lr20dp12/battery-alkaline-d-1-5v-pk12/dp/BT02614?st=lr20

[54]	‘PB320PD Power Bank Dual USB Charger with USB-C 20000mAh, Black - Ansmann | CPC’. Accessed: Mar. 16, 2025. [Online]. Available: https://cpc.farnell.com/ansmann/1700-0147/powerbank-pb320pd-20000mah/dp/BT06954

[55]	‘LiPo Battery LP7065125 10000mAh 3.7V 37Wh | LiPol Battery Co., Ltd’. Accessed: Mar. 16, 2025. [Online]. Available: https://www.lipobattery.us/lipo-battery-lp7065125-10000mah-3-7v-37wh-with-pcm-and-wires-and-jst-phr-2/?_gl=1*3z5so5*_up*MQ..*_ga*OTUxNzIxNjIxLjE3NDIxMjcyNDY.*_ga_08ZLJYQED8*MTc0MjEyNzI0My4xLjAuMTc0MjEyNzI0My4wLjAuMTAwMzUwMjk5Nw..&gclid=Cj0KCQjw7dm-BhCoARIsALFk4v9Ma7SnMzAIZuc3sgrCK9XTy_G2EG-RKud6ROzG2p5p0BfJ0mjlNH0aAl8YEALw_wcB

[56]	‘UA78M33CKCS Texas Instruments | Mouser United Kingdom’. Accessed: Mar. 16, 2025. [Online]. Available: https://www.mouser.co.uk/ProductDetail/Texas-Instruments/UA78M33CKCS?qs=0O%2FZFlpUpJW16wrDG1C6LA%3D%3D

[57]	‘TL072CP Texas Instruments | Mouser United Kingdom’. Accessed: Mar. 09, 2025. [Online]. Available: https://www.mouser.co.uk/ProductDetail/Texas-Instruments/TL072CP?qs=5nGYs9Do7G3e6Tx9uHIgUA%3D%3D

[58]	‘LM7805CT/NOPB Texas Instruments | Mouser United Kingdom’. Accessed: Mar. 09, 2025. [Online]. Available: https://www.mouser.co.uk/ProductDetail/Texas-Instruments/LM7805CT-NOPB?qs=OYMYEaN9QmBS2GvaX6GSkQ%3D%3D&utm_id=9525998811&gad_source=1&gclid=Cj0KCQiA19e8BhCVARIsALpFMgFXxNJeWuSVGJAa-ugb4Sifk3L_SPhaBk5-iw3XXhNGLEGwlOZW6ZcaAo5NEALw_wcB

[59]	‘3mm Red LED, Diffused, 18mA - Pro Signal | CPC’. Accessed: Mar. 09, 2025. [Online]. Available: https://cpc.farnell.com/pro-signal/psg91832/led-3mm-red-diffused-10-pack/dp/SC19626?mckv=sshopping_dc|pcrid|689656657184|kword||match||plid||slid||product|SC19626|pgrid|157126163454|ptaid|pla-310521768236|&CMP=KNC-GUK-CPC-SHOPPING-20992120747-157126163454-SC19626&s_kwcid=AL!5616!3!689656657184!!!network%7d!310521768236!&gad_source=1&gclid=Cj0KCQiA19e8BhCVARIsALpFMgEV_4k50mUCYzKck0yL8P1rHTMbhQbIGzAJoTXAZVBJ5sEfOZtoXH4aAo2JEALw_wcB

[60]	‘3mm Green LED, Diffused, 18mA - Pro Signal | CPC’. Accessed: Mar. 09, 2025. [Online]. Available: https://cpc.farnell.com/pro-signal/psg91833/led-3mm-green-diffused-10-pack/dp/SC19627?mckv=sshopping_dc|pcrid|689656657184|kword||match||plid||slid||product|SC19627|pgrid|157126163454|ptaid|pla-310521768236|&CMP=KNC-GUK-CPC-SHOPPING-20992120747-157126163454-SC19627&s_kwcid=AL!5616!3!689656657184!!!network%7d!310521768236!&gad_source=1&gclid=Cj0KCQiA19e8BhCVARIsALpFMgH85OXfeJ4q8YWkB-OIeA6mOh-n1WOOorx8QjdCvhd8NfV79EKiUksaAgVTEALw_wcB

[61]	‘NHD-0420AZ-FSW-GBW-33V3 Newhaven Display Intl | Optoelectronics | DigiKey’. Accessed: Mar. 09, 2025. [Online]. Available: https://www.digikey.co.uk/en/products/detail/newhaven-display-intl/NHD-0420AZ-FSW-GBW-33V3/2773596?gclsrc=aw.ds&&utm_adgroup=&utm_source=google&utm_medium=cpc&utm_campaign=PMax%20Shopping_Supplier_Newhaven%20Display_0757_Co-op&utm_term=&utm_content=&utm_id=go_cmp-20681030286_adg-_ad-__dev-c_ext-_prd-2773596_sig-Cj0KCQiA19e8BhCVARIsALpFMgFFQR86XGGul0Viz1ni_x6p5oQWF4kXqTjxwxorYx6twGemGFeZubQaAuedEALw_wcB&gad_source=1&gclid=Cj0KCQiA19e8BhCVARIsALpFMgFFQR86XGGul0Viz1ni_x6p5oQWF4kXqTjxwxorYx6twGemGFeZubQaAuedEALw_wcB&gclsrc=aw.ds

[62]	‘1009 Adafruit Industries LLC | Kits | DigiKey’. Accessed: Mar. 09, 2025. [Online]. Available: https://www.digikey.co.uk/en/products/detail/adafruit-industries-llc/1009/7241401?srsltid=AfmBOoqOJ29DJY0WXAoIBlDquwdeIbMwzB5SSTnFou8ZBkqfVxGwxSNWim4&gQT=1

[63]	‘796739-2 TE Connectivity | Mouser United Kingdom’. Accessed: Mar. 09, 2025. [Online]. Available: https://www.mouser.co.uk/ProductDetail/TE-Connectivity/796739-2?qs=DUs9f6OUnucjHXAXMBymqQ%3D%3D

[64]	‘1-826629-2 TE Connectivity | Mouser United Kingdom’. Accessed: Mar. 09, 2025. [Online]. Available: https://www.mouser.co.uk/ProductDetail/TE-Connectivity/1-826629-2?qs=FazuUmncXokmxpv%252BFZO3KQ%3D%3D

[65]	‘Capacitors - SparkFun Learn’. Accessed: Apr. 13, 2025. [Online]. Available: https://learn.sparkfun.com/tutorials/capacitors/application-examples

[66]	‘8-bit PIC® MCU Master Clear Pin External Reset - Developer Help’. Accessed: Apr. 13, 2025. [Online]. Available: https://developerhelp.microchip.com/xwiki/bin/view/products/mcu-mpu/8bit-pic/reset-options/master-clear-pin-external-reset/

[67]	‘How to Conduct a Successful Objective Evaluation - Hrider’. Accessed: Apr. 14, 2025. [Online]. Available: https://www.hrider.net/blog/8603/1/como-hacer-una-evaluacion-de-objetivos-exitosa.html

[68]	‘10 Water-Resistant Options for Your 3D Printing | Xometry Pro’. Accessed: Mar. 09, 2025. [Online]. Available: https://xometry.pro/en-uk/articles/3d-printing-water-resistant/

[69]	‘Everything you need to know about Smart Street Lighting - inteliLIGHT®’. Accessed: Apr. 16, 2025. [Online]. Available: https://intelilight.eu/smart-street-lighting/

[70]	Krusche & Company, ‘What is the Waterfall software development methodology and is it still relevant?’ Accessed: Oct. 17, 2024. [Online]. Available: https://kruschecompany.com/waterfall-software-development-methodology/

[71]	J. More, ‘Software Development Model — Incremental Development’, Bootcamp. Accessed: Oct. 17, 2024. [Online]. Available: https://medium.com/design-bootcamp/dlc-software-development-model-incremental-development-7598ae6500e6

[72]	‘960 Adafruit Industries LLC | RF and Wireless | DigiKey’. Accessed: Apr. 08, 2025. [Online]. Available: https://www.digikey.co.uk/en/products/detail/adafruit-industries-llc/960/5353630?gad_source=1&gbraid=0AAAAADrbLljAIvbeE6eJrvM5VY2FcxJlf&gclid=CjwKCAjwktO_BhBrEiwAV70jXv_WGRa2Rg5Kw7N8m6op1ak1c0ZKUKQJqLnCGteUw5Mzgprs6efWHhoCxHkQAvD_BwE&gclsrc=aw.ds

[73]	‘24LC1026 | Microchip Technology’. Accessed: Apr. 08, 2025. [Online]. Available: https://www.microchip.com/en-us/product/24lc1026

[74]	‘PIC16F887 | Microchip Technology’. Accessed: Mar. 02, 2025. [Online]. Available: https://www.microchip.com/en-us/product/PIC16F887

[75]	‘pic16f887-microcontroller-device-overview - MIKROE’. Accessed: Apr. 17, 2025. [Online]. Available: https://www.mikroe.com/ebooks/pic-microcontrollers-programming-in-assembly/pic16f887-microcontroller-device-overview

# Bibliography

| [1] | Geeks for Geeks, “C Programming Language Tutorial,” Sanchhaya Education, 06 March 2025. [Online]. Available: https://www.geeksforgeeks.org/c-programming-language/. [Accessed April 2025]. |
| --- | --- |
| [2] | B. V. Dam, PIC Microcontrollers 50 Projects for Beginners and Experts, Susteren: Elektor, 2007. |
| [3] | M. Siegesmund, Embedded C Programming, Oxford: Newnes, 2014. |
| [4] | P. Horowitz and W. Hill, The Art of Electronics, New York: Cambridge University Press, 2015. |
| [5] | N. Gardner, “Pic Micro McU: An introduction to programming The Microchip PIC in CCS C,” Ccs Inc, 2002. |
| [6] | Custom Computer Services, “CCS Forum,” phpBB , 2005. [Online]. Available: https://www.ccsinfo.com/forum/. [Accessed April 2025]. |
| [7] | W3 Schools, “C Tutorial,” Refsnes Data, 2025. [Online]. Available: https://www.w3schools.com/c/index.php. [Accessed April 2025]. |
| [8] | CCS Compiler Help Section, C Compiler, CCS, 2025. |

# Appendices

## Appendix A – PCC Street Lighting Policy

## Appendix B – Streetlighting complaints Examples

## Appendix C – PCC APSE Benchmarking Results

## Appendix D – CTA Split Core Current Transformer Datasheet

## Appendix E – Adafruit Ultimate GPS Datasheet

## Appendix F – GPS External Antenna Datasheet

## Appendix G – DC-DC Converter Datasheet

## Appendix H – EEPROM Datasheet

## Appendix I – PIC16F887 Microcontroller Datasheet

## Appendix J – LiPo Battery Datasheet

## Appendix K – 3.3V Voltage Regulator Datasheet

## Appendix L – Operational Amplifier Datasheet

## Appendix M – 5V Voltage Regulator Datasheet

## Appendix N – Red / Green LED Datasheet

## Appendix O – LCD Display Datasheet

## Appendix P – Tactile Buttons Datasheet

## Appendix Q – Fixed Terminal Block Datasheet

## Appendix R – Header Pins Datasheet

## Appendix S – Software Code

## Appendix T – Additional Part Night Information