BREEAM

UWTSD’s SA1

Waterfront development

Water assessment report for the new library

Author - Melanie Wright

University number - p166041

Date of report publication – 29th March 2018

Contents

Page

- Introduction 										3

- Why we need to conserve water							3

- The water category									4

- Methodology										4

- Results										5

- Conclusion										6

- Evidence compiled									6

- References										7

- Bibliography										7

- Appendices 									            8

- Introduction

The aim of this report is to carry out a BREEAM assessment on UWTSD’s new buildings situated down at their Waterfront Development on SA1. The designated building is the library and the designated category is water. This report is part of a collaborative group of reports that will culminate in an overall BREEAM assessment for the whole building. This report is written working in collaboration with Merlin Consultants Ltd the BREEAM assessors and Kier Construction Group, the building designers and constructors.

The remit of this report is to establish the number of credits that could be achieved in the water category for regulated water, which will then be amalgamated with all the other report findings to calculate the final rating for the building.

- Why we need to conserve water

Fresh water is an essential but diminishing resource. It is continuously being recycled through the Earths water cycle but it is being consumed quicker than it can be replaced. Climate changes are causing lakes and rivers to dry up and although water currently covers 70% of the earth, only 1% is accessible and fit for drinking water (WWF 2017).

If we consume less water then we will need to pump and treat less water. Consequently we will use less energy and chemicals and therefore we reduce our carbon emissions, which are thought to be one of the major causes of climate change (South Staffs Water, 2017).

Also the demand for water grows as the world’s population grows. The population figure currently stand at 7.5 billion people but it expected to grow to 9.8 billion by 2050 (World Resources Institute, 2017).

At the current rate of consumption two-thirds of the world’s population may face water shortages by 2025 (WWF, 2017)

On average every person in Britain uses 150 litres of water a day and most of that goes down the sewerage system (Cambridge Water Company, 2018).

Flushing a w.c. can use up to 30 litres a time (conserve h2o, 2018).

It is crucial that water is saved in this area and could be done by collecting rain water or recycling non-potable water. This is achieved by using a grey water recycling system which would involve collecting waste water from the wash hand basins and kitchenette taps, filtering and treating it, then using it to flush w.c.’s. This could reduce water consumption by 50% (Aquaco Water Recycling Ltd, 2018).

3.0	The water category

The Water category focuses on sustainable water use in buildings and the site they are located in. It looks to identify ways to reduce regulated potable water consumption for sanitary use and to recycle non-potable water which includes rainwater and greywater. The assessment carries a weighting of 7% for the library, as it is classed as a fully fitted building.

To obtain credits the assessment looks at four different aspects of water efficiency.

- WAT01 Water consumption – can achieve five credits by cutting down the amount of regulated potable water used for sanitary use. This is done by fitting efficient sanitary components, collecting rainwater and recycling water. A credit is obtained when an improvement is made above the baseline performance set by building regulations.  A BREEAM WAT01 calculator is used to assess what effect the component has on reducing water consumption by calculating the litres/person/day against the baseline. This will show what percentage of water will be saved for credits to be awarded. A saving of 12.5% is one credit, 25% two credits, 40% three credits, 50% four credits and for 55% saving five credits will be awarded. If a 65% saving is achieved then an exemplary credit will be awarded. To calculate the improvements of the water consumption these components must be of a certain specification; wc’s, urinals, taps, showers, baths, dishwashers, washing machines and any rainwater or greywater used must be specified for varying building types.

- WAT02 Water monitoring – can achieve one credit if the water is being monitored to reduce consumption. A minimum standard is for a water meter to be fitted.

- WAT03 Water leak detection – can achieve two credit. One for a leak detection system to be installed and the other for flow control devices to be fitted to all sanitary fittings.

- WAT04 Water efficient equipment – can achieve one credit if all the unregulated water uses are identified and reduced.

4.0       Methodology

The assessment process started with the technical specifications and drawings for the library being supplied by Merlin Consultants. These documents contain the plans and the BREEAM specifications for each category.

The specifications and information received was introduced into the assessment of the BREEAM UK New Construction technical manual (2014) for Non-domestic Buildings.

For Water Consumption five credits are potentially available. The specifications for the performance levels of each of the sanitary ware that has been installed into the library was provided. The plans show that the following services have been installed into the library:

- Ground floor – 7 wc’s and 7 wash hand basins (whb’s) plus one kitchenette with taps

- First floor – 6 wc’s and 6 whb’s.

- Second floor – 6 wc’s and 6 hwb’s plus one kitchenette plus taps

- Third floor – no services

There are no urinals or showers in this building – this confirmation was sought from Jamie Best, Merlin Consultants.

For water consumption the following information was provided and put into the WAT01 calculator, which will calculate the amount of credits awarded.

- WC’s 3.75 litres – effective flush volume

- WHB taps 3.75 litres/minute

- Kitchenette tap 5 litres/minute

There were no urinals so the drop box in B28 had to be altered to reflect this information.

There were no rain water or grey water recycling systems identified.

Information was given for the other three aspects of the water category. However to assess for credits the information given has to be backed up by hard evidence. This evidence demonstrates compliance, the level of performance and the rating. This evidence was requested from Jamie Best, Merlin Consultants who visited UWTSD to give a talk. The evidence requested was:

- Design & post construction plans

- Communication records

- Construction methodology

- Environmental policy

- Formal letters of correspondence

- Minutes of meetings

- Drawings

- Component specifications

- Site visits/inspection reports

- Photographic evidence

- Manufacturers information

- Product details

The other three sections specifications (water monitoring, water leak detection and water efficient equipment) were compared against the BREEAM standards.

5.0	Results

Water Consumption -The minimum standards has to have a baseline of “good” as opposed to a “pass” to achieve any credits in this section and the water calculator has to be used for the assessment. From the information provided the specifications for the wc’s, whb and kitchenette taps were put into the water calculation (see appendix 1). When compared against the base level standards in table 36 these specifications were found to have a perceived performance level rating of four credits, out of a maximum of five credits.  However the calculations from the water calculator only award a potential three credits because there is no evidence that a specified rain water or grey water system have been installed.

Water Monitoring - the minimum standards have been achieved because a water meter has been installed.  Then any plant or area that consumes more than 10% of the whole buildings water consumption is fitted with sub meters or water monitoring equipment to ensure monitoring and management compliance. Therefore the one available credit could potentially be obtained because the water is being monitored to reduce consumption.

Water Leak Detection - a leak detection system to detect major leaks within or to the library has been installed and flow control devices that regulate the supply of water to each sanitary fitting have been installed. These are rated at one credit each so potentially the two available credits could be obtained.

Water Efficient Equipment – reducing unregulated water consumption by utilising water efficient equipment is not specified but the external landscaping relies solely on precipitation so this could potentially achieve the one available credit.

6.0	Conclusion

When we compared the component specifications against table 36 for water consumption it appeared that a rating of 4 credits could potentially be awarded. However when all the figures for the components were put into the water calculator only 3 credits could potentially be awarded. To achieve a rating of 5 out of 5 credits for the Water Consumption, the components would have had to be more efficient. The wc would need to use only 3 litres instead of 3.75 litres and the whb use 3 litres/minute instead of 3.75 litres/minute. The kitchenette tap is already the most efficient specification. Also rainwater and greywater recycling systems would have to be installed that comply with the specified requirements.

The final potential rating for the whole water category is:

Water Consumption - 3 credits

Water Monitoring – 1 credit

Water Leak Detection – 2 credits

Water Efficient Equipment – 1 credit

Altogether the overall possible number of credits that could potentially be awarded are 7 credits out of a possible total of 9 credits. This equates to 63% of the total credits achievable which equates to a potential weighting of 4.4% out of the total weighting of 7%.

7.0 	Evidence compiled

The following evidence was supplied by Merlin Consultants:

BREEAM Specifications – containing the component specifications for the wc, hwb and kitchenette taps. These specifications are the calculations required for the Water Calculator (appendix 1).   See appendix 2.

WAT01 calculator – as assessed by Jamie Best. Required as part of the minimum standards for WAT 01. See appendix 3.

Stride Treglown Architecture – outlining all the sanitary appliances and fittings specifications and manufacturers codes. See appendix 4.

Letter from Kier Construction to Merlin Consultants – confirming the appointment of Jamie codes Best as the Sustainability Champion for the construction stage, who is responsible for ensuring the compliance with BREEAM targets. This is not rated under water but is essential to the whole  BREEAM assessment. See appendix 5.

Terms of reference – minutes from the project board committee to set out the strategic direction and management of the project. See appendix 6.

Environmental Policy Statement – clarifies the strategy for sustainability and states “conserve water by reducing demands at our sites and premises”. See appendix 7.

Proposed Domestic Water Schematic – diagrams of the water systems. See appendix 8.

RIBA Stage 3 Civil and Structural Engineering Report – clarifies the drainage, incorporating surface water drainage, water quality and foul water drainage. See appendix 9.

Letter from Kier Construction to Merlin Consultants – confirming the surface water run-off as specified on the drawings. See appendix 10.

Drainage Strategy – setting out the proposed foul and surface water drainage and the compliance with BREEAM. It states that the proposed development aspires to achieve a BREEAM rating of Excellent, which can only be assessed when all the reports are compiled. To achieve a rating of excellent 70% rating would be required. See appendix 11.

Proposed Drainage Layout – shows the plans for the proposed drainage on site. See appendix 12.

Letter from UWTSD to Merlin Consultants – confirming that a post occupancy evaluation will be carried out by an independent third party. This includes the sustainable performance of water consumption. See appendix 13.

8.0 	Reference

Aquaco Water Recycling Ltd (2018). Retrieved 26th March 2018 from https://www.aquaco.co.uk/grey-water-recycling/residential/

Cambridge Water Company (2018). Retrieved 21st March 2018, from http://www.cambridge-water.co.uk/customers/how-much-water-do-you-use

Conserve h2o org (2018). Retrieved 21st March 2018, from https://www.conserveh2o.org/toilet-water-use

South Staffs Water (2017). Retrieved March 21st 2018, from https://www.south-staffs-water.co.uk/help-and-advice/read/how-does-saving-water-help-the-environment-200100000002621

World resources institute (August 24th 2017). Retrieved 21st March 2018, from http://www.wri.org/blog/2017/08/7-reasons-were-facing-global-water-crisis

WWF   (June 26th, 2017). Retrieved March 21st 2018, from https://www.worldwildlife.org/threats/water-scarcity

9.0	Bibliography

9.1 Websites

BREEAM (2017). Retrieved 27th February 2018, from www.breeam.com

BRE Ltd (2017). Retrieved 27th February 2018, from www.bre.co.uk

European Environmental Agency (2018). Retrieved 21st March 2018, from

https://www.eea.europa.eu/themes/water/wise-help-centre/glossary-definitions/water-stress

Government of Saskatchewan (2018). Retrieved 21st March 2018 from www.environment.gov.sk.ca/ConservingWater

List Den (March 13th 2014). Retrieved 21st March 2018, from http://listden.com/top-10-reasons-why-we-must-save-water/

USGS (2nd December 2016). Retrieved 21st March 2018 from

https://water.usgs.gov/edu/qa-home-percapita.html

9.2 Manuals

BRE Global Ltd (2014). BREEAM UK New Construction, Non-domestic Buildings (UK). Technical Manual. SD5076(5.0) p219-241

10.0	Appendices

Appendix 1 – 	WAT01 calculator resulting from this report

Appendix 2 - 	BREEAM Specifications and component specifications

Appendix 3 - 	WAT01 calculator – as assessed by Jamie Best

Appendix 4 - Stride Treglown Architecture outlining all the sanitary appliances and fittings specifications

Appendix 5 –	 Letter confirming Jamie Best as the Sustainability Champion

Appendix 6 – 	Terms of Reference

Appendix 7 – 	Environmental Policy Statement

Appendix 8 - 	Proposed Domestic Water Schematic

Appendix 9 - 	RIBA Stage 3 Civil and Structural Engineering Report

Appendix 10 -	Letter confirming the surface water run-off

Appendix 11 - 	Drainage Strategy

Appendix 12 - 	Proposed Drainage Layout

Appendix 13 - Letter to Merlin Consultants confirming that a post occupancy evaluation will be carried out