Emma Bergson P148476

Energy Management & Efficiency (M6X01197)

# Energy Audit of Bloomfield Community Centre

Contents

1	Introduction	3

2	Background to the company	4

3	Types of energy used and where it is used	5

3.1	Space and Water Heating	5

3.2	Lighting	5

3.3	Insulation and Draught-proofing	6

3.4	Grade II Listed Building	6

4	Assessment of the current situation	7

4.1	Baseline energy consumption	7

4.2	Patterns of operation and the work practices	9

5	Calculations of the amount of energy used	10

5.1	Water Heating	10

5.2	Playschool Room and Jackson Room Fabric Heat Loss Investigation	11

6	Discussion of potential energy savings that can be obtained	13

6.1	Space and Water Heating	13

6.1.1	Space heating	13

6.1.2	Water Heating	13

6.1.3	Renewable Heating Incentive (RHI)	14

6.2	Lighting	16

6.3	Insulation and draught proofing	16

7	Recommendations	17

8	References	18

Table 1 Table showing figures to nearest 100 of light and heat total expenditures from tax year 2012/13 to 2018/19 (NDCSA, 2013 - 2019)	8

Table 2. Electricity consumption, 2019	9

Table 3. Gas consumption for 2019	10

Table 4. Data displaying inputs and results of immersion heating	12

Table 5. Playschool Room total fabric heat loss calculations	13

Table 6. Jackson Room total fabric heat loss calculations	13

Table 7. STS cost recoup figures	14

Table 8. ASHP cost recoup	15

Table 9. FMEA on the water heating system	16

Table 10. Improved U-values for the Playschool Room	17

Table 11. Improved U-values for the Jackson Room	17

Figure 1.Chart displaying light and heat total expenditures from tax year 2012/13 to 2018/19 (NDCSA, 2013 - 2019)	8

Figure 2. Line chart displaying total electricity consumption, 2019	9

Figure 3. Line chart displaying total gas consumption, 2019	10

Equation 1	11

Equation 2	11

Equation 3	11

# Introduction

This report is comprised of a brief description of the charity organisation; Narberth & District Community & Sports Association (NDCSA) and the building it operates in; Bloomfield House Community Centre, which gives details of a grade II listed building and their limits. It investigates the types of energy in the building and how and where this energy is used. A general assessment of the current situation is included and a FMEA on water heating alternatives. It also covers a more in-depth investigation into the listed part of the building, calculating fabric heat loss for two of the main rooms. It concludes with some recommendations for improvements for potential energy savings.

At the time of the report the UK was still in the European Union (EU) and utilises the Energy Performance of Buildings Directive 2010 (EUR-Lex, 2018) to analyse efficiencies.

# Background to the company

Bloomfield house was built as a private manor house in 1819. Between 1953 and 1979 it was owned and used by local government.  When the district council proposed selling Bloomfield house a community campaign resulted in the town council purchasing the site in 1980 and leasing it to the Narberth and District Community Association, now NDCSA.  Since 1980 a series of renovation and extension projects have been undertaken, resulting in quite a large and complex building. The old part of the building is grade II listed (Perkins, 2019).

Activities are varied including Adult Education classes and regular room hire for private clubs and societies. There are a range of sports facilities including a recently installed Recreation Hall, newly refurbished fitness suite, two squash courts and a sports hall. There are a number of offices, some of which are leased out to the local authority. There is a day care centre for local elderly people and also a nursery and after school club for young children. The centre has an average annual footfall of 150,000 and is generally in use from 8:00 – 22:00 Monday to Friday, 9:00 – 17:00 Saturday and 9:00 – 13:00 on Sundays (Perkins, 2019).

# Types of energy used and where it is used

As mentioned before the building is comprised of several extensions onto a 200 year old Grade II listed manor house. Electricity is billed for the entire building and gas is separated into three areas; old building, new building and recreation hall.

The new building refers to the most recent extension which was completed in 2005 and comprises a seminar room with a kitchen on the ground floor and toilets, two classrooms and an office on the first floor. Built to modern energy standards this won’t be included in the audit but should be considered when looking at the electricity consumption.

The recreation hall replaced an old air dome and has recently been updated with LED lights, it uses overhead electric heaters to heat the room in the winter. It has solar panels on the roof which brings in a Feed in Tariff payment on average of £600 per annum, this supports payments for the electricity used.

The area under consideration known as the old building, uses grid electricity for lighting, power and water heating and mains gas for space. The rooms vary in size, insulation and types of lighting.

## Space and Water Heating

Following a Carbon Trust Energy Audit in 2004 the centre upgraded its heating system in 2006, switching from electric storage heaters and an old oil boiler to a mains gas central heating system. The old building is now heated by 2 mains gas condensing boilers, which were replaced from the original boilers in 2017. The heating system has a good controls package that includes thermostatic radiator valves, zone thermostats and zoned programmers. At present the programmers aren’t used, the heating is switched on manually and controlled using the zoned thermostats. The boilers are serviced annually when the heating system is switched back on after a short break during the warmer months. The sports hall is heated by one large ceiling mounted gas powered radiant heater.  The squash courts have a similar set up, however, they have an external gas bottle supply.  They both work well and are only used in the colder months.

## Lighting

Many of the corridors and the rooms have strip lighting of various sizes and wattage and other areas use energy saving bulbs. After having a professional consultation, the centre is currently undergoing lighting improvements switching from fluorescent strips and bulbs to using more efficient LED lighting.  This is being done in phases due to the initial cost.

## Insulation and Draught-proofing

Insulation levels are generally far better in the newer parts of the centre however a complete understanding of wall cavity information is unknown. Loft insulation has been installed in the old building and lagging surrounds all water pipes.

## Grade II Listed Building

There are many restrictions on listed buildings regarding any changes to the exterior and sometimes the interior, according to Pembrokeshire County Council this is to, ‘… ensure on-going care and protection for important buildings.’ (Pembrokeshire County Council, 2018). A large area of the centre is listed Grade II and has many old single glazed sash windows in the centre, a primary cause of heat loss with a high U-value of 5W/m² (Pullen, 2009).  The listed status of the building would make it incredibly hard to completely replace the windows.

# Assessment of the current situation

To make a general assessment of the centre, their accounts from 2013 – 2019 were made available. In the accounts both light and heat expenditures are grouped together, figure 1 displays this information with a following table which goes into more detail of the costs.

Figure 1.Chart displaying light and heat total expenditures from tax year 2012/13 to 2018/19 (NDCSA, 2013 - 2019)

Table 1 Table showing figures to nearest 100 of light and heat total expenditures from tax year 2012/13 to 2018/19 (NDCSA, 2013 - 2019)

| Year | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Cost (£) | 28200 | 15700 | 20400 | 17500 | 15400 | 19500 | 21900 |

During 2013 construction of their new Recreation Hall was undertaken to replace the very inefficient Air Dome, this explains the dramatic decrease in the total expenditure 2012/13 to 2013/14. The result of completing the new Recreation Hall gave them an annual saving of £8,000 in their gas bill which is reflected in the 2014/15 total. One of the main reasons for the increase in total expenditure is due to their new suppliers not recognising the organisation as a charity and charging the full 20% VAT instead of 5%.

## Baseline energy consumption

2019 electricity and gas consumption can be found in figures 2 and 3. As expected, both daytime electricity and gas consumption reduce during the lighter warmer months.  They currently have a night-time tariff for their electricity which is fairly stable.

Figure 2. Line chart displaying total electricity consumption, 2019

Table 2. Electricity consumption, 2019

| Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Daytime (kWh) | 8399 | 7864 | 7769 | 5967 | 5877 | 6373 | 5029 | 4728 | 5590 | 6933 | 7862 | 6999 |
| Night-time (kWh) | 960 | 932 | 912 | 835 | 948 | 987 | 879 | 963 | 1074 | 1219 | 1343 | 1216 |

Figure 3. Line chart displaying total gas consumption, 2019

Table 3. Gas consumption for 2019

| Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Consumption (kW/h) | 11440 | 8930 | 8964 | 6436 | 2936 | 400 | 0 | 0 | 190 | 5537 | 9452 | 7445 |

## Patterns of operation and the work practices

With the centre offering such a wide variety of activities it is open 364 days a year, however, with many of the users attending adult education classes, the After School Club and after school clubs it does have considerably more usage during school term time. The centre has a monthly average footfall of 12,000 in the quieter non term time months and a larger figure of 15,000 in term time.

The daytime consumption is vastly due to water heating; the current water heating system uses an immersion heater which is estimated to use 3100 kW per month.

Another major energy consumer will be the lighting. The centre is currently going through a lumens inspection with areas already having LED lighting fitted, these include the larger rooms of the sports hall and Recreation Hall and part of the upstairs including corridors and classrooms.

Overnight appliances such as a large community fridge and freezer will be the main sources of energy used during the night-time tariff.

# Calculations of the amount of energy used

Some assumptions have been made with the following data.

## Water Heating

One of the largest consumers of electricity for the centre is the current water heating system, it uses an electric immersion heater which consumes a lot of energy. The centre needs to provide hot water throughout the day for the public showers and toilets, Day Care Centre and Nursery. Exact calculations cannot be provided however table 4 contains data based on heating mains water from 15°C to 60°C with the assumption that a total of 5 hours out of the 15 they’re open the water will need to be heated. The remaining 19 hours are based on keeping the temperature between 50-60°C to prevent legionella and assume 100% efficiency. Equations 1-3 were used to complete the calculations, 4.2 in equation 1 is the constant specific heat capacity of water rounded to 1 decimal place (Sust-it, n.d.).

Equation 1

Power used (kWh)=4.2 x tank capacity litres x temperature increase (°C)3600 seconds

Equation 2

Time taken hours= Power Used (kWh)Immersion heater power rating (kW)

Equation 3

Cost £=Time taken hours x electricity unit cost£ x immersion heater power rating (kW)

With an average monthly energy consumption of 7638kWh at a cost of £1440, Table 4 shows that an average monthly total of £450, just under a third, is due to heating water. Finding a more efficient way to do this will not only reduce cost but also reduce carbon emissions.

Table 4. Data displaying inputs and results of immersion heating

|  |  | Reaching temp when in use (5 hours) | Maintaining Temp |
| --- | --- | --- | --- |
| Element | Unit | Amount | Amount |
| Tank capacity (2x250l) (L) | l | 500.00 | 500.00 |
| Element (1 x 18kW and 1x19kW) | kW | 37.00 | 37.00 |
| Starting Temperature (T) | °C | 15.00 | 50.00 |
| Final Temperature (T) | °C | 60.00 | 60.00 |
| Temperature difference (ΔT) | °C | 45.00 | 10.00 |
| Thermal power (Pt) | kWh | 26.25 | 5.83 |
| Time to heat (t) | h | 0.71 | 0.16 |
| Day rate | £/kWh | 0.14 | 0.14 |
| Night rate | £/kWh | 0.10 | 0.10 |
| Charge for 1 hour during day | £ | 3.57 | 0.79 |
| Charge for 1 hour during night | £ | 2.56 | 0.57 |
| Charge for day | £ | 12.67 | 1.50 |
| Charge for night | £ | 0.00 | 0.63 |
| Charge for month | £ | 385.46 | 64.76 |

## Playschool Room and Jackson Room Fabric Heat Loss Investigation

A more in-depth analysis has been completed on the ‘front’ of the house (grade II listed) which contains the Playschool Room (PSR) and the Jackson Room (JR). Due to the age of the listed part of the building, 200 years, focus for the PSR and JR will be on fabric heat loss and how to improve the insulation. This area of the building is already in the process of switching to the more efficient LED’s after having a professional lumen inspection.

The PSR and JR are situated in what’s known at the centre as the front of the house, it being the main entrance to the old manor house. They have the same floor space but differ in height. The PSR has an access door and an internal double door, both are wooden with glass panels. It has two single glazed sash windows and four radiators. Upstairs the JR has solid wood double doors, three single glazed sash windows and three radiators. The heating is controlled by a thermostat. The PS room is used almost constantly from 8:30 – 18:30, sometimes all the way through to 22:00.

Tables 5 and 6 calculate the total fabric heat loss with the PS and JR having a fabric heat loss of 4.8kW and 5.3kW respectively, U-values have been estimated using a table of U-values obtained from www.puravent.co.uk (Puravent, 2020). The temperature (T) difference has been calculated for the colder months (October to March) with the internal T controlled at 20°c and the outside T has used four years of data (2015 – 2018) to gain the average of each month and then averaged the total (Tiseo, 2019).

Table 5. Playschool Room total fabric heat loss calculations

| Playschool Room Element |  | U Value (W/m²) | Area (m) | ΔT (°C) | Rate of heat loss (W) |
| --- | --- | --- | --- | --- | --- |
| 2 single glazed windows |  | 4.8 | 4 | 13 | 249.60 |
| Wooden door with glass panels to outside |  | 3.9 | 2.88 | 13 | 146.02 |
| Inside double wooden door with glass panels |  | 3.9 | 3.6 | 13 | 182.52 |
| Floor (concrete) |  | 0.8 | 63.8 | 13 | 663.52 |
| Ceiling (floor of JR) |  | 1.7 | 63.8 | 13 | 1409.98 |
| Internal walls |  | 1.5 | 32.36 | 13 | 631.02 |
| External stone walls |  | 2 | 59.58 | 13 | 1549.08 |
|  |  | Total fabric heat loss W |  |  | 4831.74 |

Table 6. Jackson Room total fabric heat loss calculations

| Jackson Room Element |  | U Value (W/m²K) | Area (m) | ΔT (°C) | Rate of heat loss (W) |
| --- | --- | --- | --- | --- | --- |
| 3 single glazed windows |  | 4.8 | 4.86 | 13 | 303.26 |
| Solid wood double door |  | 3 | 3.4 | 13 | 132.60 |
| Floor (ceiling of PS) |  | 1.7 | 63.8 | 13 | 1409.98 |
| Ceiling (into roof) |  | 1.7 | 63.8 | 13 | 1409.98 |
| Internal walls |  | 1.5 | 29.08 | 13 | 567.06 |
| External stone walls |  | 2 | 58.42 | 13 | 1518.92 |
|  |  | Total fabric heat loss W |  |  | 5341.80 |

# Discussion of potential energy savings that can be obtained

## Space and Water Heating

### Space heating

The current heating system using gas is suitable to the task.

### Water Heating

After finding leaks within an old water heating system a modern unvented indirect cylinder system was installed in January 2019. It comprises of two connected 250l tanks with one primary coil rating 18kW and one 19kW. This being a large source of energy use, an FMEA (table 9) has been done on installing a Solar Thermal System (STS) or Air Source Heat Pumps (ASHPs), the results follow.

#### Solar thermal system

The centre has a lot of roof space and could make use of this by installing an STS. Some of the benefits of using an STS is the all year round solution, just using some extra heat from the existing immersion heater during the winter months. Using a free energy source, the Sun, will reduce the energy bills, anything up to 60% (Energy Saving Trust, n.d.). At that rate it would take just over 11 years to recoup the installation costs, estimated at £55,000 (Vasili, 2020), at today’s rate for power. It would be eligible for the Government’s Renewable Heating Incentive (RHI) (Gov.uk, n.d.) shortening the time to recover the cost.  They would not have to worry about energy prices increasing (GOV.uk, n.d.) and it will reduce CO2 emissions reducing the organisations carbon footprint (Energy Saving Trust, n.d.).

Table 7. STS cost recoup figures

| Solar Thermal System |  |  |  |
| --- | --- | --- | --- |
| Year | Cost recoup | Energy used | Cost saving |
| 1 | £55,000.00 | £1,080.52 | £4,322.07 |
| 2 | £49,597.42 | £1,080.52 | £4,322.07 |
| 3 | £44,194.83 | £1,080.52 | £4,322.07 |
| 4 | £38,792.25 | £1,080.52 | £4,322.07 |
| 5 | £33,389.67 | £1,080.52 | £4,322.07 |
| 6 | £27,987.08 | £1,080.52 | £4,322.07 |
| 7 | £22,584.50 | £1,080.52 | £4,322.07 |
| 8 | £17,181.92 | £1,080.52 | £4,322.07 |
| 9 | £11,779.33 | £1,080.52 | £4,322.07 |
| 10 | £6,376.75 | £1,080.52 | £4,322.07 |
| 11 | £974.17 | £1,080.52 | £4,322.07 |
| 12 | -£4,428.42 | £1,080.52 | £4,322.07 |

#### Air source heat pumps

Absorbing heat from the outside, Air source heat pumps (ASHPs) are a new low carbon alternative to heat buildings and provide hot water. With their energy source constantly being renewed they have minimal environmental impact (Energy Saving Trust Ltd, n.d.). Dimplex predicts their water heater will use five times less electricity; assuming the claims of five times reduction to be correct, installation cost of an estimated £20,000 (Dimplex) would take just over 8 years to recoup and would also be eligible for the RHI (Gov.uk, n.d.).

Table 8. ASHP cost recoup figures

| Air Source Heat Pumps |  |  |  |
| --- | --- | --- | --- |
| Year | Initial cost | Energy used | Cost saving |
| 1 | £20,000.00 | £1,080.52 | £4,322.07 |
| 2 | £16,758.45 | £1,080.52 | £4,322.07 |
| 3 | £13,516.90 | £1,080.52 | £4,322.07 |
| 4 | £10,275.35 | £1,080.52 | £4,322.07 |
| 5 | £7,033.80 | £1,080.52 | £4,322.07 |
| 6 | £3,792.25 | £1,080.52 | £4,322.07 |
| 7 | £550.70 | £1,080.52 | £4,322.07 |
| 8 | -£2,690.85 | £1,080.52 | £4,322.07 |

### Renewable Heating Incentive (RHI)

Both STS and ASHPs are eligible for the Government’s Non-Domestic RHI, table 9 shows the different tariffs available for 2019/20 (Ofgem, 2020), they are quoted in kilo Watt thermal hours i.e. for every kilo Watt thermal hour produced they will reimburse the amount shown. Installing an STS system will bring nearly 4 times as much income as the ASHP, however with such a large initial cost this still wouldn’t make it more cost viable.

Table 9. FMEA on the water heating system

| FMEA |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Process/Product Name: |  | Water Heating System |  |  |  | Prepared By: |  |  | Emma Bergson |  |  |  |  |  |  |
| Responsible: |  | Project Leader |  |  |  | FMEA Date (Orig.): |  |  | 12-Jan | (Rev.): | 31-Jan-20 |  |  |  |  |
| Process Step/Input | Potential Failure Mode | Potential Failure Effects | SEVERITY (1 - 10) | Potential Causes | OCCURRENCE (1 - 10) | Current Controls | DETECTION (1 - 10) | RPN | Action Recommended | Resp. | Actions Taken | SEVERITY (1 - 10) | OCCURRENCE (1 - 10) | DETECTION (1 - 10) | RPN |
| What is the process step, change or feature under investigation? | In what ways could the step, change or feature go wrong? | What is the impact on the customer if this failure is not prevented or corrected? |  | What causes the step, change or feature to go wrong? (how could it occur?) |  | What controls exist that either prevent or detect the failure? |  |  | What are the recommended actions for reducing the occurrence of the cause or improving detection? | Who is responsible for making sure the actions are completed? | What actions were completed (and when) with respect to the RPN? |  |  |  |  |
| Water heating system | Using too much electricity | Electricity bill rising | 4 | Old technology | 10 | Monthly bills | 3 | 120 | Investigate ASHPs | Project leader | Full investigation made and information passed onto the relevant people, 3/2/20 ASHP estimated instalment £20,000 Uses 5 x less energy RHI = 2.75 p/kWhth | 7 | 2 | 1 | 14 |
|  |  |  | 4 | Old technology | 10 | Monthly bills | 3 | 120 | Investigate SHSs | Project leader | Full investigation made and information passed onto the relevant people, 3/2/20 ASHP estimated instalment £55,000 Uses up to 60% less energy RHI = 10.98 p/kWhth | 8 | 2 | 2 | 32 |

## Lighting

The lighting is already under review so will not be included here.

## Insulation and draught proofing

Insulating listed buildings can be difficult if permission is needed to change anything on the interior, luckily Bloomfield House doesn’t have such stipulations. Internal Wall Insulation (IWI) can be created to improve the thermal resistance of an old building (McCraig, Pender, & Pickles, 2018). Pavadentro is an IWI Board that can be plastered directly and will improve the U-value by 0.9W/m² (Pavadentro).

Another form of draught proofing is to add secondary glazing to the windows, again this can be difficult for a listed building (Mynors, 2006) but not impossible and could improve the U-value by 2.8W/m² (Pullen, 2009).

An improvement in U-values will decrease the energy needed to warm and maintain heat in the rooms, this will in turn reduce the carbon emissions of the centre.

Table 10. Improved U-values for the Playschool Room

| Playschool Room Element | U-value (W/m²) | Area (m) | ΔT (°C) | Rate of heat loss (W) |
| --- | --- | --- | --- | --- |
| 2 single glazed sash windows with secondary glazing shutters | 2.00 | 4.00 | 13.00 | 104.00 |
| Wooden door with glass panels to outside | 2.00 | 2.88 | 13.00 | 74.88 |
| Solid wood double door | 3.00 | 3.60 | 13.00 | 140.40 |
| Floor (concrete) | 0.80 | 63.80 | 13.00 | 663.52 |
| Ceiling (floor of JR) | 1.70 | 63.80 | 13.00 | 1409.98 |
| Internal walls | 1.50 | 32.36 | 0.00 | 0.00 |
| External stone walls x 3 with internal insulation | 0.60 | 59.58 | 13.00 | 464.72 |
|  | Total fabric heat loss W |  |  | 2857.50 |

Table 11. Improved U-values for the Jackson Room

| Jackson Room Element | U Value (W/m²K) | Area (m) | ΔT (°C) | Rate of heat loss (W) |
| --- | --- | --- | --- | --- |
| 3 single glazed sash windows with secondary glazing shutters | 2.00 | 4.86 | 13.00 | 126.36 |
| Solid wood double door | 3.00 | 3.40 | 13.00 | 132.60 |
| Floor (ceiling of PS) | 1.70 | 63.80 | 13.00 | 1409.98 |
| Ceiling (into roof) | 1.70 | 63.80 | 13.00 | 1409.98 |
| Internal walls | 1.50 | 29.08 | 0.00 | 0.00 |
| External stone walls x 3 with internal insulation | 0.60 | 58.42 | 13.00 | 455.68 |
|  | Total fabric heat loss W |  |  | 3534.60 |

# Recommendations

After a thorough investigation the following recommendations will be put forward.

To improve the amount of energy used heating water they should replace their current system with an ASHP. Not only will this reduce their energy bill it will reduce their carbon emissions. With the reduced bill they could cover the cost of installation within 9 years. If they take up the option of the Government’s RHI scheme this time would be reduced.

To improve the heat loss in the Playschool Room and Jackson Room they should put secondary glazing on the windows and install IWI on the walls. This will improve the U-value by 2.8W/m², not only will this reduce the heating needed it will reduce the carbon footprint of the building.

Finally, they should look into finding a new supplier, one that would recognise them as a charity, this would save them 15% on their electricity bill.

# References

Dimplex. (n.d.). Edel Hot Water Heat Pump. Retrieved January 31, 2020, from www.dimplex.co.uk: https://www.dimplex.co.uk/sites/default/files/assets//EDL%20UK%20data%20sheet%20v0.5.pdf

Energy Saving Trust Ltd. (n.d.). Air source heat pumps. Retrieved from https://energysavingtrust.org.uk: https://energysavingtrust.org.uk/renewable-energy/heat/air-source-heat-pumps

Energy Saving Trust. (n.d.). Solar Water Heating. Retrieved January 15, 2020, from https://energysavingtrust.org.u: https://energysavingtrust.org.uk/renewable-energy/heat/solar-water-heating

EUR-Lex. (2018, 12 24). EUR-Lex Access to European Union Law. Retrieved from https://eur-lex.europa.eu/: https://eur-lex.europa.eu/legal-content/EN/ALL/;ELX_SESSIONID=FZMjThLLzfxmmMCQGp2Y1s2d3TjwtD8QS3pqdkhXZbwqGwlgY9KN!2064651424?uri=CELEX:32010L0031

GOV.uk. (n.d.). Industrial energy price statistics. Retrieved January 25, 2020, from www.gov.uk: https://www.gov.uk/government/collections/industrial-energy-prices

Gov.uk. (n.d.). Non-domestic Renewable Heat Incentive (RHI). Retrieved January 31, 2020, from www.gov.uk: https://www.gov.uk/non-domestic-renewable-heat-incentive

McCraig, I., Pender, R., & Pickles, D. (2018). Energy Efficiency and Historic Buildings: How to Improve Energy Efficiency. Historic England Publishing.

Mynors, C. (2006). Listed Buildings, Conservation Areas and Monuments . London: Sweet 7 Maxwell.

NDCSA. (2013 - 2019). Report of the Trustees and Unaudited Financial Statements, Years Ended 31 March 2013 - 31 March 2019 . Llewelyn Davies, Chartered Accountants.

Ofgem. (2020, 29 January). Non-Domestic RHI tariff table (Q4 - 2019/20). Ofgem.

Pavadentro. (n.d.). Pavadentro Data Sheet. Retrieved January 14, 2020, from www.acaraconcepts.com: https://www.acaraconcepts.com/wp-content/uploads/2015/09/Data-Sheet-Pavadentro-2017.pdf

Pembrokeshire County Council. (2018, January 24). Listed Buildings and Conservation Area, Listed Buildings. Retrieved January 27, 2020, from www.pembrokeshire.gov.uk: https://www.pembrokeshire.gov.uk/listed-buildings-and-conservation-area/listed-buildings

Perkins, J. (2019, December 2). Manager. (E. Bergson, Interviewer)

Pullen, T. (2009, June 3). Windows: single, double or triple glazing. Retrieved January 26, 2020, from www.yougen.co.uk: http://www.yougen.co.uk/blog-entry/1324/Windows%273A+single%272C+double+or+triple+glazing/

Puravent. (2020, January 26). L1 Appendix A: Tables of U-Values. Retrieved from www.puravent.co.uk: http://www.puravent.co.uk/Guide_Resources/AppendixA_UValues.pdf

Sust-it. (n.d.). Electric Immersion Water Heater Running Costs Calculator. Retrieved January 2020, from www.sust-it.net/: https://www.sust-it.net/immersion-heater-energy-calculator.php

Tiseo, I. (2019, September 5). Monthly average daily temperatures in the United Kingdom (UK) from 2015 to 2019 (in degrees Celsius). Retrieved January 12, 2020, from www.statista.com: https://www.statista.com/statistics/322658/monthly-average-daily-temperatures-in-the-united-kingdom-uk/

Vasili, A. (2020). Commercial Solar Panel Systems (4kW-100kW). Retrieved January 31, 2020, from www.theecoexperts.co.uk: https://www.theecoexperts.co.uk/business-energy/commercial-solar-panels