## Slide 1: Energy Auditing
By
Andrew Thorn

## Slide 2: Energy Audit
An energy audit is a feasibility study to establish and quantify the cost of the various energy inputs to, and flows within a facility or organization over a given period
The overall aim of an energy audit is to identify viable and cost effective energy measures which will reduce operating costs

## Slide 3: Energy Auditing
Energy audits can take a variety of forms, but the process usually involves collecting data from energy invoices and meters, and undertaking surveys of plant, equipment and buildings, as well as collecting information from managers and other staff
The auditing process should identify ways to enhance an organization’s operating efficiency and decrease its maintenance costs.

## Slide 4: Energy Audits
Should help to resolve any occupant comfort issues
An energy audit should be viewed as the ‘foundation’ on which any future energy management programme is built
Energy management programmes involve the continual monitoring and targeting of energy consumption

## Slide 5: Energy Auditing
Before targets can be set, or effective monitoring undertaken, it is important to establish:
Baseline energy consumption
Patterns of operation and the work practices used
The condition of the organization’s buildings, plant and equipment
Energy management opportunities, which will result in energy cost reductions

## Slide 6: Energy Auditing
An energy audit should identify those issues which need immediate direct action, as well as those which require further detailed investigation
It should also produce data, which can be used to justify future capital investment, and raise, within the organization, general awareness of energy conservation matters
The financial benefits afforded to an organization by an energy audit are both direct and indirect

## Slide 7: Energy Auditing
The direct benefits are fairly obvious; energy cost savings can be achieved by reducing consumption, or simply by changing tariff or fuel types
The indirect benefits are much less obvious; reduced maintenance costs will arise from improved plant utilization and reduced operating hours
Also, improved plant utilization may result in the estimation of excess plant capacity and ultimately reduced capital expenditure

## Slide 8: Energy Auditing
The auditing process should identify energy management opportunities, which when implemented will result in financial benefit to an organization
The magnitude of these financial benefits is not necessarily dependent on the level of capital investment
In many situations can be achieved through the implementation of ‘no cost’ or low cost measures

## Slide 9: Energy Auditing
No cost or low cost measures
Changing an energy tariff
Rescheduling production activities to take advantage of preferential tariffs
Adjusting existing controls so that plant operation matches the actual requirements of the building or manufacturing process

## Slide 10: Energy Auditing
No cost or low cost measures
Implementing good housekeeping policies in which staff are encouraged to avoid energy wasteful practices
Investment in small capital items such as thermostats and time switches
Although much can be achieved through low cost measures, it is sometimes necessary to undertake more capital-intensive measures, such as replacing worn out plant

## Slide 11: Types of Energy Audit
Energy audits can broadly be classified as preliminary, targeted and comprehensive audits
Each type is distinguished by the level of detail involved and the depth of the analysis undertaken
It is important to select the appropriate audit type for the facility concerned

## Slide 12: Types of Energy Audit
Comprehensive audits involve detailed energy surveys of plant, equipment and the fabric of buildings, which is a time consuming and expensive process
They therefore should not be undertaken lightly
It is often better to focus detailed surveys on problem areas highlighted by a preliminary energy audit, otherwise much time and money can be wasted

## Slide 13: Types of Energy Audit
By carrying out a preliminary audit and methodically applying a range of simple analysis techniques it is often possible to identify major energy problems without the need for expensive and detailed energy surveys
Preliminary energy audits seek to establish the quantity and cost of each form of energy used in a facility or in an organisation

## Slide 14: Types of Energy Audit
Preliminary Audit
They are relatively quick and are designed to determine a project’s potential
Preliminary audits are primarily concerned with obtaining data from energy invoices and meter readings for a given period

## Slide 15: Types of Energy Audit
Targeted energy audits often result from preliminary audits
They provide data and detailed analysis on specific targeted projects
For example, an organisation may target its lighting installation or boilers with a view to up-grading these items of equipment
Targeted audits therefore involved detailed surveys of the target subjects and analysis of the energy flows and costs associated with the targets

## Slide 16: Energy Audits
Comprehensive energy audits provide detailed data on the energy inputs to, and energy flows within a facility
They should produce detailed energy project implementation plans
Such audits involve detailed energy surveys and may involve the use of complex energy simulation computer software

## Slide 17: Why is Energy Wasted
Poorly designed buildings and installations
Buildings maybe poorly insulated resulting in high space heating costs
Mechanical ventilation ducts may be undersized so that fan power consumption is high
Heating systems may be installed without any optimum start control
Time clock controllers may be incorrectly set so that buildings are heated when not in use

## Slide 18: Why is Energy Wasted?
Inefficient plant operation, often arising from the use of old or out of date technology, a situation often made worse by poor maintenance
Poor operating and working practices. Lights are often left on in buildings when they should be switched off

## Slide 19: Main Reasons for Energy Wastage
Building designers do not pay energy bills
The design process is closely allied to the construction process, and designers usually select low capital cost solutions, which often result in higher operating costs
This situation is made worse by the fact that the budgets for constructing a facility and running it are usually completely separated

## Slide 20: Main Reasons for Energy Wastage
Energy consumption is taken for granted
Most building occupants and users do not pay energy bills
They are concerned with their own personal comfort and are not particularly interested in how much energy is consumed in achieving a comfortable environment
Most organisations do not have a culture of energy efficiency

## Slide 21: Energy Savings
Much energy wastage arises from poor strategic and operational management
Lack of energy saving culture amongst staff
Energy can often be saved at no capital expense simply by improving maintenance procedures and instigating good work practices

## Slide 22: What is an Energy Survey
A systematic review of how energy is used within a building or industrial site
An energy survey is a technical investigation of the control and flow of energy in a (1) site; (2) building; (3) process/manufacturing unit and; (4) piece of equipment

## Slide 23: What an Energy Survey Covers
Energy conversion: - for example, gas to heat in a boiler, electricity to cooling in a chiller
Energy distribution: - how energy gets from one place to another
Energy end use: - the equipment and people that use the energy
Management systems: - how energy is managed and accounted for

## Slide 24: When to Undertake a Survey
Ideally you should undertake your first survey as part of the development of your energy strategy, at the beginning
This means that you’ll be able to set objectives based on concrete knowledge of how energy is being used, rather than guesswork
Practices and technology change, so you should consider undertaking a full energy around every five years

## Slide 25: When to Undertake a Survey
An efficient energy survey will establish which areas will need regular attention and review through good continuing energy management
When planning the timing of energy surveys, take account of any asset condition surveys that are planned as the two can support each other

## Slide 26: Survey Framework
Three key elements are:
Review your energy usage
Identify energy saving opportunities
Define practical next steps

## Slide 27: Review Your Energy Usage
The starting point for this is the main points of supply: electricity meters, gas meters, oil tank etc.
By analysing your bills you can find out how much of each energy supply you use
You can then ‘track’ the energy from each point of supply to its point of end use

## Slide 28: Identify Energy Saving Opportunities
Keep your eyes open for wastage- usually the easiest saving opportunity to spot
For example, you might not be sure if one type of light is more efficient than another, but it will be very clear if a light is on that does not need to be
If you find out that your boiler is 20 years old it would be fair to assume there are more efficient alternatives available

## Slide 29: Define Practical Next Steps
A survey on its own will not save any energy
It is up to you to act on the findings
A good survey will result in a list of practical next steps, presented in a way that encourages action

## Slide 30: Energy Survey Process
Establish current patterns of overall consumption and expenditure at site level
Do meaningful energy ratios (performance indicators) exist for your sector
Calculate the figures for your site. If your ratios are higher than those published this may indicate your savings potential

## Slide 31: Energy Survey Process
Tabulate where you have examples of particular services and processes and use this to manage your on-site survey activity.
Visit each area or department and look for things which are obviously wrong and need to be corrected
Identify opportunities which may apply to your site in particular
If you are not sure what to look at first, start with the principal central services and the largest process users
By measurement, experiment, or interference, estimate the present energy use of particular systems and plant, and likely potential savings in each case

## Slide 32: Energy Survey Process
Discuss potential energy saving solutions with suppliers and obtain quotations
Calculate the financial viability of the projects you are proposing, and present recommendations to those who need to give approval
Report your findings, and put into action any low-cost and no-cost measures you have identified

## Slide 33: Energy Survey Report Format
Summary: - A brief narrative introducing the survey, its findings and recommendations and the action plan
Introduction: - Background to the site and its operations
Energy use and expenditure statistics
If appropriate and available, the trend in energy performance indicator(s) or benchmark(s)

## Slide 34: Energy Survey Report Format
Survey findings: - Detailed discussion of findings, presented either by area, or by technology theme
Recommendations: - (1) measures to be taken; (2) expected costs; (3) grants and incentives; (4) estimated savings; (5) non-energy benefits; (6) implementation risks and risk mitigation; (8) payback periods

## Slide 35: Identify Lighting Saving Opportunities
Current Practice | Recommendation(s)
People not knowing where the lights switches are | Education and information via a staff awareness and motivation campaign
Empty areas lit unnecessarily | Fit more switches per bank of lights, if wiring permits
Large banks of lights controlled by a single switch | Introduce occupancy controls, especially in infrequently occupied rooms

## Slide 36: Identify Lighting Saving Opportunities
Current practice | Recommendation(s)
Tungsten filament lamps | Unless these are specialist lamps, these should be changed to energy efficient types
Older “Switch start” and larger diameter tubes (T12 and T8) fluorescent lighting | Replacing fixtures with more efficient equivalents using T5 lamps and high-frequency
Excessive light levels for the type of work being done | Reduce lamp ratings, remove or safely disconnect ‘redundant’ lights. Redesign and replace lighting

## Slide 37: Identify Lighting Savings Opportunities
Current Practice | Recommendations
‘Redundant’ lights, i.e. fittings that were originally installed, but don’t now serve a purpose | Remove or safely disconnect ‘redundant’ lights
Artificial lighting in areas with sufficient daylight | Daylight sensors, or photocells, can be used for external lighting or for internal areas with good access to daylight
Dirty or discoloured diffusers, reflectors and shades | Introduce adequate lighting maintenance and cleaning regimes

## Slide 38: Heating and Hot Water
Heating and hot water can account for as much as 60% of your total energy costs
Because it’s possible to reduce your heating costs by up to a third, the potential savings are substantial
Check that monthly fuel demand varies in accordance with changing weather

## Slide 39: Heating and Hot Water
A 1°C drop in average space temperature can cut heating energy consumption by about 8%
Temporary data logging can provide valuable evidence. As a minimum, aim to record the inside and outside air temperature at 10 minute intervals
For ‘wet’ systems, record the boiler casing or flue temperature to detect when the system starts and stops

## Slide 40: Heating and Hot Water
Check circulation temperature to ensure that heat distribution is appropriately controlled
You can estimate the rate of heat loss from a building from the rate of temperature decay when the heating, lights and equipment are turned off at the end of the day
Establish the number of full-time occupants and how they use hot water to estimate their requirements

## Slide 41: Heating and Hot Water Saving Opportunities
Current practice | Recommendations
Heating outside working hours | Adjust existing times and other controls Fit 7-day programmable controllers Consider optimum start/stop control
Excessive space temperatures | Consider re-balancing the heating system to prevent some areas being overheated Fit improved heating system controls and TRVs

## Slide 42: Heating and Hot Water Saving Opportunities
Current practice | Recommendations
Unauthorised supplementary electric heating | Educate users and investigate why the area in question is cold
Mechanical ventilation running when building is unoccupied | Fit seven day programmable controllers
Mechanically ventilated buildings | Investigated the possibility of increased recirculation Consider ventilation heat recovery

## Slide 43: Heating and Hot Water Saving Opportunities
Current practice | Recommendations
Frost protection thermostats set too high | Reset to appropriate level
Heating and cooling being used simultaneously | Investigate ‘dead band’ settings
Anything which restricts heat output, including blocked grills, obstructed radiators, clogged air filters | Introduce improved maintenance regimes

## Slide 44: Heating and Hot Water Saving Opportunities
Current practice | Recommendations
Vehicle access doors which may be left open for long periods | Consider interlocking loading bay doors with heating Fast acting roller shutter doors, or secondary doors to create an air lock
Summer immersion heaters running simultaneously with boilers, or at risk of doing so | Fit point of use water heaters with time control to dispense with central storage and long distribution runs

## Slide 45: Boilers and Heat Distribution
Current practice | 
Irregular boiler and heating system maintenance regime | Regular annual service of boilers and heating systems can save 10% or more of heating costs
Multiple boilers sharing loads when fewer units could meet the demand | Install boiler sequence control, or rectify faults in existing sequence control
Ageing boiler plant | If boilers are over 15 years old consider replacing them with more efficient types
Flooding in pipe ducts | Check duct drainage is effective

## Slide 46: Boilers and Heat Distribution
Current practice | Recommendations
Check that boiler time clock settings are correct | Reset as necessary
Could boilers be running when there is no demand other than their own standing losses? | Improving control so that boilers are only enabled when there is demand from one or more of the circuits served
Check for water losses by assessing the water make-up rate | Investigate for leaks and repairs

## Slide 47: Boilers and Heat Distribution
Current practice | Recommendations
Steam leaks | Repair
Steam traps passing steam or not passing condensate | Eliminating bypass valves on steam traps and if necessary fitting better-matched traps
Manual temperature control of process items | Fitting automatic temperature controls in place of manual valves

## Slide 48: Boilers and Heat Distribution
Current practice | Recommendations
Condensate running to waste | Investigating possibilities for recovery
Manual control of dissolved solids | Implementing automatic TDS (Total Dissolved solids) control on boilers Increasing feedwater

## Slide 49: Boilers and Heat Distribution
Current practice | Recommendations
Dead lengths of pipework, or long runs of pipework with very small demands at the end | Rationalising pipework to reduce distances travelled (and reduce diameter where feasible) and remove dead pipe runs Making alternative provision for small loads at the ends of long dedicated pipe runs (or relocating them)
Flash steam being lost from receivers | Finding a use for flush steam (e.g. sparging it into the feedwater tank or cascading to lower pressure users)

## Slide 50: Ventilation
Good ventilation is essential- it provides fresh air and also helps protect your building against damp and condensation
It is also needed to remove fumes and pollution from occupied areas
If you can’t see or hear the fans, check air movement by hanging thin strips of tissue paper near extract grilles

## Slide 51: Ventilation Saving Opportunities
Current practice | Recommendations
Local extract ventilation running when not required | Adjust timer settings where installed. Install time controls where appropriate
Clogged or obstructed grilles or filters | Implement proper maintenance and cleaning schedule
Inadequate use of existing air-recirculation facilities | Investigate and increase air-recirculation to

## Slide 52: Ventilation Saving Opportunities
Current practice | Recommendations
Dampers being used to control air flow rates | Consider variable speed drives (VSD) control of the fans instead
No heat recovery from exhaust air | Investigate the visibility of introducing heat recovery from exhaust air to incoming fresh air
Old inefficient fans and poor efficiency motors | Fit higher efficiency fans and motors- for existing fans this normally only makes sense when the motor fails

## Slide 53: Air Conditioning
Observe the operating patterns of air conditioning chillers, cooling towers, etc. relative to outside conditions
Compare refrigerant suction/discharge temperatures and condenser water temperatures on similar plant items. Look for excessive running or frequent on/off cycling
Keep a log of when the chiller is running to spot whether it’s being used during cool weather

## Slide 54: Air Conditioning Saving Opportunities
Current practice | Potential Opportunities
Heating and cooling being used simultaneously | Adjust temperature set points and investigate ‘dead band’ settings to avoid simultaneous heating and cooling
Lack of time control, excessive hours of operation or risk of time schedule being overridden | Implement appropriate time control to avoid unnecessary cooling. Make sure controls can’t be adjusted by unauthorised people
Air re-circulation potential not exploited or very low | Investigate and increase air-recirculation to suitable levels, balancing energy conservation against air quality

## Slide 55: Air Conditioning Saving Opportunities
Current practice | Potential Opportunities
Overheating of Occupied space due to solar heat gain | Consider using blinds and/or solar film to reduce heat gain in summer Consider solar shading for air conditioned building areas
Air exchange with non-conditioned spaces | Improve isolation of conditioned from non-conditioned spaces; e.g. add doors, fit door closures etc.
Doors and windows being left open, gaps in building structure, or other infiltration routes | Repair gaps, fit door closures as appropriate. Educate building occupants via awareness campaign

## Slide 56: Air Conditioning Saving Opportunities
Current practice | Potential Opportunities
Excessively tight control of relative humidity where not essential | Adjust settings Discontinue control of relative humidity where possible
Blocked filters and/or fouled evaporator or condenser coils | Implement proper maintenance and cleaning regimes
Zones where cooling is required all year round rather than just in summer | Consider providing ‘spot cooling’ systems for zones with year-round cooling requirements, so that the main control system just needs to be operated seasonally

## Slide 57: Motors and Drives
Thermal imaging equipment can help you pinpoint frictional transmission losses, poor electrical connections
The temperature of a motor can indicate the load it is working under
Start with the largest motors and longest running hours

## Slide 58: Motors and Drives Saving Opportunities
Current practice | Potential Opportunities
Oversized motors: check whether motors are appropriately sized for their duty | If permanently lightly loaded, compare efficiency figures with smaller high efficiency motors to see whether replacement will be cost effective
Motors in poor condition | Fit high-efficiency motors when replacements are necessary
Worn or slack V-belts | Replace worn belts or pulleys. Re-tension slack belts

## Slide 59: Motors and Drives Saving Opportunities
Current practice | Potential Opportunities
Risk of unnecessary running | Improve machinery operator control and education Introduce time switching, or control via other sensors or BMS Fit automatic stop/start control (this might include motor load sensing)
Misaligned pulleys or couplings | When V-belt pulleys need replacing consider conversion to wedge belts or synchronous flat, or ribbed belts Repair/Realign misalignments

## Slide 60: Motors and Drives Saving Opportunities
Current practice | Potential Opportunities
Worn bearings in motors, driven equipment, or intermediate drive train | Repair and maintain to reduce losses and risk of failure Use high-performance lubricants
Voltage imbalance, low or high voltages, harmonic distortion or poor power factor | Correct to optimise efficiency
Fixed speed motors used for variable load applications | Consider VSDs- best savings are with fans, pumps and air compressors