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1. [bookmark: _Toc211519943]
Introduction
Testing benches for industrial ovens are used for assessing and guaranteeing compliance and safety requirements. PLCs, which are integrated into commercial test rigs, have always been a major component of such testing infrastructure[1]. PLC-based systems have a number of disadvantages despite their shown robustness[2]. They frequently limit scalability and adaptation to the particular requirements of oven specific testing due to their high upfront cost, reliance on vendor specific software, and complex maintenance[3]. For businesses that need flexibility, cost effectiveness, and functionality that is specifically adapted to their needs, relying on general purpose industrial solutions leads to wasteful spending.

By challenging the dependence on PLC-only solutions and suggesting the creation of a unique controller intended especially for oven testing applications, this study aims to overcome these constraints. Crucially, this method offers a number of clear benefits, including a substantial cost reduction, hardware and software customisation, the addition of oven specific features like direct MCB feedback and thermocouple interfacing, and the ability to expand in response to changing needs.

Up to seven oven sockets and two main contactors will be supported by the suggested system architecture, which will be managed by nine separate outputs. With real-time MCB status tracking, emergency stop functionality, and sensor integration. Feedback will be provided via voltage sensors, current transformers, and a Type-K thermocouple. Through monitoring, system is able to identify abnormalities like overloads or overheating and immediately switch to a safe shutdown mode.

The controller will use RS232, which is widely used[9], to communicate and control with a PC. Operators will be able to watch and control oven testing in real time thanks to the PC program.  An DC-DC converter stage will regulate the 24 V supply power to 5 V and 3.3 V for the controller's circuitry.

The ultimate goal of this project is to provide an oven specific testing solution that is modular, safe, and economical. It offers an alternative to expensive PLC-based systems by combining affordability and expandability, which makes it a desirable small-to-medium businesses that require dependable yet adaptable oven testing.


2. [bookmark: _Toc211519944]Aim and Objectives
[bookmark: _Toc211519945]2.1 Aim:
Design, build, and evaluate a custom controller for a testing station that test industrial ovens. Sensor monitoring, RS232-based PC connectivity for data exchange, and contactor control that directs load to sockets chosen by the PC will all be integrated by the controller. Along with complying to relevant electrical and safety regulations in the UK and USA, it will also feature automatic fault protection.

[bookmark: _Toc211519946]2.2 Objectives:
[bookmark: _Toc211519947]2.2.1 Ensure compliance and implement safety mechanisms
By monitoring emergency stop signals, adding watchdog protection, and ensuring adherence to PUWER 1998[10], BS EN 61439[11], IEC 60204-1[12], and IEC 62061/ISO 13849[13].
[bookmark: _Toc211519948]2.2.2 Design and implement reliable output control
By implementing a reliable output control system for the controller. And use N-channel MOSFET drivers to ensure safe, reliable switching.
[bookmark: _Toc211519949]2.2.3 Integrate and test sensor monitoring and data acquisition
By interfacing with current, voltage, and temperature sensors, applying signal conditioning, and enabling real-time measurement.
[bookmark: _Toc211519950]2.2.4 Develop PC communication
To enable real-time transfer of sensor data, system status, and control commands.
[bookmark: _Toc211519951]2.2.5 Evaluate system expandability/cost-effectiveness
Use a modular architecture to support additional oven channels or future functional upgrades.
Keep total system cost within reasonable budget while ensuring reliability, robustness, and long-term serviceability.

3. [bookmark: _Toc211519952]Background Research
[bookmark: _Toc211519953]3.1 PLCs in industrial automation
PLC’s have long been the cornerstone of industrial automation, providing durability, modular design, and strong vendor support[1]. They enable reliable operation under demanding conditions through standardized input/output modules, built-in diagnostics, and programming via ladder logic[5]. PLCs continuously monitor input signals from devices such as sensors, execute programmed logic, and control actuators or other equipment based on these inputs[2][3]. Inputs from sensors are processed, outputs drive actuators, motor starters. Industrial protocols allows PLCs to communicate with other PLCs or HMIs. Control logic can be programmed in different way, offering flexibility in implementation[3][5]
[bookmark: _Toc211519954]
3.2 Limitations of PLCs
In many scenarios, the full functionality of a PLC is not required, leaving much of the system not used. High hardware costs, software licensing fees, and vendor specific support increase the initial investment. Closed architectures reduce interoperability and can lead to complex maintenance requirements[3]. These limitations have motivated my research into alternative control solutions for industrial test benches.
[bookmark: _Toc211519955]3.3 Alternatives: PCs and Embedded Controllers
PCs and controllers are emerging as cost-effective, flexible alternatives. PCs offer higher computational power, large-scale data storage, and versatile software development platforms, allowing integration of multiple serial communications and fully integrated HMI solutions[6][7]. However, PCs do not have internal relays or switches to control components such as contactors, which are required for testing station power distribution.

For instance, Ahshan et al. developed a microcontroller-based control system for a small induction-generator wind turbine. The study highlighted that while a PLC could have been used, an embedded solution was more cost-effective, met computational requirements, and avoided unnecessary hardware complexity. While embedded systems are highlighted as cost-effective in specific study[8], most existing research is not addressing safety interlocks and PC-based monitoring.
[bookmark: _Toc211519956]3.4 Research gap for test benches
PLCs remain the dominant choice in industrial automation[1], their high cost, limited flexibility, and complexity make them less suitable for specialized appliance testing environments[3]. Existing literature shows a lack of modular, low-cost controllers that combine real-time monitoring, PC-based connectivity, safety interlocks, and appliance-specific functionality.





4. [bookmark: _Toc211519957]Project Desing
The suggested system is designed as a controller that is integrated into a testing bench. Hardware architecture, software development, safety and compliance protocols, testing procedures, and risk assessment are all covered in the project design.
4.1 Hardware Architecture
The PIC18F46J50 is the main part of the controller in Figure 1 Hardware Architecture. It was chosen due to sufficient I/O ports, and UART functionality for RS232 connection[14]. The I/O expander will be used to get around its limited number of I/O pins, communicating via I²C. MOSFETs control the controller's outputs by powering contactors and relays. The input signals consist of three current transformer analogue inputs, three voltage sensor analogue inputs, one Type-K thermocouple input, six auxiliary MCB feedback inputs that have been scaled from 24 V to 3.3 V via voltage dividers, and one emergency stop input that has also been reduced to 3.3 V. The 24 V system input will be stepped down into 5 V and 3.3 V rails for the controller and peripherals using an DC-DC converter.
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[bookmark: _Ref209690401]Figure 1 Hardware Architecture


[bookmark: _Toc211519958]4.2 Firmware and Software Design
Using the MPLAB X IDE, firmware will be created in C to handle functions including input monitoring, socket switching logic, communication, and emergency shutdown procedures. Figure 2 Firmware flowchart shows how it should operate. 
[image: ]
[bookmark: _Ref209690556]Figure 2 Firmware flowchart
[bookmark: _Toc211519959]4.3 Safety and Compliance
Compliance with PUWER[10], BS EN 61439[11], and IEC 62061[13] will act as the foundation for safety design, guaranteeing that all systems meet accepted safety requirements. By monitoring on MCBs through their auxiliary terminals, the controller will be able to quickly identify and address any issues. The emergency stop feature will instantly stop controller functioning and put the system in a safe state, going beyond software-based shutdowns.



[bookmark: _Toc211519960]4.4 Testing Methodology and Risk Management
Socket and contactor switching will be verified by bench testing, and reference meters will be used to calibrate sensors for precise readings. MCB tripping and emergency stop activations will be simulated in safety tests, and the dependability of RS232 communication will be evaluated under load. A watchdog and repeated testing will be used to control firmware failures, thermal hazards will be minimised by thermocouple monitoring, and electrical hazards.
[bookmark: _Toc211519961]
4.5 Ethical Implications
Operators of testing station are protected from electrical risks by internal fuse and emergency stop mechanisms that will shut down whole system when needed. Accurate measurements, sensor calibration, dependable firmware, and strong RS232 connection are all necessary to guarantee data integrity. Clear warnings, documentation, and adherence to standards all help to promote responsible use.
[bookmark: _Toc211519962]
4.6 Environmental and Societal Impact
Industrial ICs with low power consumption and optimised switching, such as MOSFETs and DC-DC converters, are used in the system to save energy and reduce components necessary. Electronic waste can be reduced by choosing durable parts and ICs with built in features. In terms of society, the controller improves oven safety by avoiding accidents and offers accurate testing data that supports safer industrial products with better output.
[bookmark: _Toc211519963]
4.7 Data Analysis and Result Evaluation
Digital inputs, RS232 communication logs, and analogue measurements (temperature, voltage, and current) are all part of the data collection. The relationship between the controller and PC will be evaluated using analysis. 
By comparing outcomes with those from calibrated reference devices, the accuracy of the thermocouple will be confirmed. Sensor outputs will be summarised through data analysis. The evaluation also includes performing repeated reliability tests, confirming measured values against expected ranges, and assessing RS232 performance under load.

5. [bookmark: _Toc203119241][bookmark: _Toc211519964]Planning
Table 1 BOM shows all resources used in the project. With the commercial discount, the cost is £60.48. For comparison, the cheapest PLCs on the market are typically priced between £300-£500[15], representing a saving of approximately 80%.
[bookmark: _Ref210725115]Table 1 BOM
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6. [bookmark: _Toc211519965]Planning
Table 2 Gannt chart table, was created outlining the key phases and tasks required to complete the project in order to guarantee an organised and effective approach. The chart outlines the six primary phases of the project: planning, design and component selection, physical build and assembly, system integration and testing, and documentation. Each phase has specific subtasks with predefined start times, durations.
[bookmark: _Ref210725818]Table 2 Gannt chart
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7. [bookmark: _Toc211519966]Expected Outcome
The project is set to deliver fully working controller prototype that can safely and reliably switch nine outputs, including two main contactors and seven sockets. The system's emergency stop mechanism, MCB auxiliary input detection, and complete safety monitoring will guarantee operational stability. Real-time temperature, voltage, and current monitoring will be carried out and dedicated PC software will be used to record and show all sensor data. 
Feedback reporting and command-based operation are made possible by RS232 communication, which enables easy interaction with external systems. The feasibility of the design within a reasonable budget will be confirmed by a comprehensive cost analysis. This controller aims to provide a cost-effective and scalable alternative to PLC-based oven testing systems. At least comparable performance will be offered by PC connectivity, safe socket switching, and real-time data recording. 
The expected benefits include an 80% cost reduction, a scalable and open structure free from vendor lock-in, tailored features optimised for oven testing, and simpler operation and maintenance. Ultimately, the study will demonstrate that microcontroller-based embedded controllers can outperform PLC-based systems in specific scenarios where cost, customisation, and flexibility are more crucial than overall industrial scalability.
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