Improving Effluent Management through Automation

by

Scott Thomas

Supervisor: Starlin Jacob

Project submitted as part of the requirements for the award of

BEng (Hons) Electrical and Electronics Engineering

April 2025

DECLARATION

I, Scott Thomas declare that I am the sole author of this Project; that all references cited have been consulted; that I have conducted all work of which this is a record, and that the finished work lies within the prescribed word limits.

This work has not previously been accepted as part of any other degree submission.

Date :  28/04/2025

FORM OF CONSENT

I Scott Thomas hereby consent that my Project, submitted in candidature for the B.Eng. (Hons) Electrical & Electronics degree, if successful, may be made available for inter-library loan or photocopying (subject to the law of copyright), and that the title and abstract may be made available to outside organisations.

Date : 28/04/2025

Abstract

This project aims to automate the effluent pumping systems at Tata Steel to improve the current manual operations, which are facing several inefficiencies. The existing system depends on manual monitoring and control, leading to higher labour costs, the risk of equipment damage, and challenges in meeting environmental regulations. To tackle these issues, the plan is to integrate Programmable Logic Controller (PLC) technology, which will allow for remote monitoring and automatic regulation of sump levels.

Research shows that automation can bring significant benefits, such as improved operational efficiency, reduced human error, and better compliance with environmental standards. A thorough literature review highlights successful case studies in similar industries and provides insights into best practices for effective implementation. This project also considers the regulatory requirements, ensuring it adheres to relevant electrical and environmental regulations.

The transition to an automated system will be divided into phases: planning, implementation, and evaluation, with a strong emphasis on minimising disruptions to operations will establish key performance indicators to evaluate how automation impacts both system efficiency and employee productivity.

Ultimately, this project not only aims to modernise Tata Steel's effluent management processes but also aspires to set a precedent for future automation efforts within the organisation, contributing to improved operational performance and environmental stewardship.

Table of Contents

Chapter 1: Introduction	10

1.1 Introduction	10

1.2 Background	10

1.3 Solution	12

1.3.1 Benefits of the Automation Project	13

1.4 Methodology	13

1.5 Limitations	13

1.6 Chapter Summary	14

Chapter 2: Research & literature Review	15

2.1 Research & literature Review	15

2.2 Automation Technologies in Effluent Management	15

2.3 Remote Monitoring and Control	16

2.4 Operational Efficiency and Resource Allocation	16

2.4.1 Legislative Compliance Context	17

2.5 Environmental Compliance	17

2.6 Ethics of automation	18

2.7 Electrical Compliance and Safety Standards	18

2.7.1 HSG253 – The safe Isolation of Plant and Equipment	18

2.7.2 Tata Steel Low Voltage rules EIS 7	18

2.7.3 IEC 61131 Standard	19

2.7.4 Machine Safety Standards	19

2.8 Technology Selection Justification & Integration Strategy	19

2.9 Chapter Summary	20

Chapter 3: Research, development & Methodology	22

3.1 Research, development & Methodology	22

3.2 Development & Methodology	22

3.2.1 Feasibility Assessment	22

3.2.2 Technology Assessment	23

3.2.3 System Design	23

3.2.4 Integration and Commissioning	23

3.2.5 Training and Knowledge Transfer	24

3.2.6 Regulatory Compliance and Environmental Impact	24

3.2.7 Lean Six Sigma Implementation	24

3.3 Data Collection	25

3.4 Project Planning	26

3.5 Components selection	29

3.5.1 PLC Selection	29

3.5.2 HMI Selection	31

3.5.3 Cable Selection	33

3.5.4 Control Panel Components	33

3.5.5 Tools & Installation Aids	33

3.5.6 Safety & Labelling	34

3.5.7 Sensors	34

Chapter 4: Design and implementation	35

4.1 Design and implementation	35

4.1.1 Overview of Key Hardware	35

4.1.2 PLC and Panel Installation	35

4.1.3 Field Instrumentation	36

4.1.4 Communication and Integration	36

4.2 Safety Considerations	37

4.2.1 Electrical isolation	37

4.2.2 Control safety	37

4.2.3 Personnel safety	38

4.2.4 Environmental	38

4.2.5 Management of change	38

4.2.6 Testing of system	39

4.2.7 Documentation and training	39

4.2.8 Installation & Commissioning Task Summary	40

4.2 Implementation	41

4.2.1 Pump panel installation	41

4.2.3 PLC network set up and Coding	44

4.2.4 AOI Available Pump Counter	44

4.2.5 AOI Dual Transmitter Selector	48

4.2.6 AOI E300 Interface	51

4.2.7 AOI Pump Manager	56

4.2.8 A – Scaling	63

4.2.9 B – Pump Selection	64

4.2.10 C – Level Control	67

4.2.11 D – Pump Management	80

4.2.12 Main Routine	83

4.2.13 HMI	84

Chapter 5 – Evaluation	88

5.1 System Testing and Results	88

5.2 Efficiency Gains	88

5.3 Compliance and Safety	88

5.4 Issues Faced	88

5.5 Operational Metrics from SAP	88

Chapter 6 – Conclusion	91

Chapter 7 Reflection	92

Chapter 8 References	93

Appendices	98

Appendix 1 – Sump Layout	98

Appendix 2 – Risk Assessment	99

Appendix 3 – Bill of Materials	101

Appendix 4 – Isolation Procedure	102

Appendix 5 – Single line diagrams	116

Appendix 7 – Images of project	128

Appendix 8 – Training and Handover	132

Table of Figures

Figure 1 – Overview of No.2 Sump and LSO	11

Figure 2 – Graph of Predicted benefits	12

Figure 3 – SAP maintenance log	26

Figure 4 – Gant chart before changes	27

Figure 5 – Gantt change after changes	28

Figure 6 – iFIX Effluent screen	36

Figure 7 – Isolation process	37

Figure 8 – SLD of plan	41

Figure 9 – Before and after for panel internal controls and power controls	42

Figure 10 – Panel Final Layout After Refurbishment	43

Figure 11 - AOI – Available Pump Counter Overview Diagram	44

Figure 12 - ST Code Structure for Pump Availability Logic	45

Figure 13 ST Code	45

Figure 14 - Pump Availability Logic Loop Initialization	46

Figure 15 - Counting Available Pumps Using FOR Loop	46

Figure 16 - Increment Pump Count on Availability Check	46

Figure 17 - Loop Termination and Count Finalization	47

Figure 18 - Output Assignment for Available Pumps Count	47

Figure 19 - Final Pump Availability Output Mapping	47

Figure 20 – Dual Transmitter AOI overview	48

Figure 21 - Dual Transmitter Selection – Tag List Overview	49

Figure 22 - Transmitter 1 Manual Selection Logic	49

Figure 23 - Transmitter 2 Manual Selection Logic	50

Figure 24 - Dual Transmitter Fault Alarm Logic	50

Figure 25 - Dual Transmitter Fault Reset from HMI	50

Figure 26 - E300 Interface – Relay Ladder Integration	51

Figure 27 - E300 Interface – Function Block Diagram	52

Figure 28 - E300 Interface – Tag mapping	53

Figure 29 - E300 Scaling ladder logic	54

Figure 30 - E300 Voltage monitoring logic	55

Figure 31 - AOI Pump Manager – Relay Ladder Diagram	56

Figure 32 - AOI Pump Manager – Function Block Diagram	57

Figure 33 - Pump fault and timer preset logic	58

Figure 34 - Overload fault detection	58

Figure 35 - Contactor fault logic	59

Figure 36 - Manual/Remote mode logic	60

Figure 37 - Interlock and availability logic	61

Figure 38 - Start/Stop relay logic	61

Figure 39 - Timeout logic initiation	62

Figure 40 - Final timeout reset logic	62

Figure 41 - Scaling block example with mA signal conversion	63

Figure 42 - Duty shift priority logic	64

Figure 43 - Duty shift temporary storage	64

Figure 44 - Duty shift priority application	65

Figure 45 - Priority transfer logic	65

Figure 46 - AOI Pump selection logic	65

Figure 47 - Dual transmitter selection AOI	66

Figure 48 – End of ladder	66

Figure 49 - Range and bandwidth calc logic	67

Figure 50 - Start/stop level setting for pumps	67

Figure 51- Bandwidth assignment per pump stage	68

Figure 52 - Stage running check logic	70

Figure 53 - Pump sequencing with delay	72

Figure 54 - Stage delay implementation	76

Figure 55 - Pump level mapping for HMI	79

Figure 56 - Start/Stop span logic across levels	82

Figure 57 - Main Routine – JSR call logic	83

Figure 58 - Firmware checks for SCADA	83

Figure 59 - Tag List Developed Prior to HMI Programming	84

Figure 60 - Initial Mock-up of HMI Layout	85

Figure 61 - Refined HMI Layout Concept	85

Figure 62 - Finalised HMI Interface Deployed to Panel	86

Figure 63 - Final HMI Testing with Revised Pump Icons	86

Figure 64 - Final Programming View with Crimson Software	87

Figure 65 - Sump layout	98

Figure 66 - Project Risk Assessment	100

Figure 67 - Bill of Materials	101

Figure 68 - Example pump 1 control diagram	116

Figure 69 - Example pump 1 diagram continued	117

Figure 70 - PLC IO	118

Figure 71 - Pump 1	119

Figure 72 - PLC Panel	120

Figure 73 - Panel External Circuits	121

Figure 74 - Junction Box FLT	122

Figure 75 - Junction Box INST	123

Figure 79a – Before work started	128

Figure 79b – After work complete and PLC installed	128

Figure 79c – New cabinet fitted.	128

Figure 79d – New and existing cables re-glanded, new containment (tray) installed.	128

Figure 83a – Before panel wiring upgrade.	129

Figure 83b – Part way through install.	129

Figure 83c – Wiring completed; final works ongoing.	129

Figure 83d – PILZ relay ready to test.	129

Figure 87a – Plate cut to size and holes in correct location.	130

Figure 87b – Installed buttons and labels	130

Figure 87c – ready for wiring.	130

Figure 87d – Installed face plate under isolation.	130

Figure 91a – Before upgrade. Old overload and CTs	131

Figure 91b – After install, new contactor and overload.	131

Figure 91c – Earth bonding completed	131

Figure 91d – Bonding & cable protection.	131

Table of Tables

Table 1 – Gantt Chart summary	28

Table 2 - PLC Selection	30

Table 3 – HMI Selection	32

Table 4 - Overview of components	35

Table 5 – Risk Assessment break down	40

Table 6 – Operator improvement	89

Table 7 – Record of meetings	132

# Chapter 1: Introduction

## 1.1 Introduction

Managing effluent effectively in industrial environments is essential for meeting environmental regulations and ensuring operational efficiency. At Tata Steel, the manual operation of the effluent pumping system has uncovered several issues, such as high labour requirements, risks of equipment failure, and difficulties in staying compliant with environmental standards. This project aims to automate the pumping system by integrating advanced Programmable Logic Controller (PLC) technology to address these challenges [1].

A significant aspect of this project is that the No. 2 sump operates as a manned pump house. However, recent organisational changes at Tata Steel have led to staff being reassigned to other areas, which has reduced the number of personnel on-site. The main goal of this project is to ensure that the operations and compliance of No. 2 sump are not compromised by these staffing cuts. By introducing automation, it can ensure that the sump continues to meet environmental standards and maintain its operational output, even with fewer staff.

The proposed automation will focus on enabling remote monitoring and automatic regulation of the pumping systems, which will ensure consistent performance while minimising operational risks. This initiative aims to lessen the need for constant on-site presence, allowing Tata Steel to uphold compliance with environmental regulations. Additionally, the project will examine the challenges of the current manual system, review literature on automation in effluent management, and analyse best practices from other industries. By modernising the operations of No. 2 sump, this will lay the groundwork for future automation projects that support Tata Steel’s commitment to sustainability and continuous improvement [2].

## 1.2 Background

Tata Steel depends on water from the River Afan, Castell and Kenfig rivers, and the Eglwys Nunydd reservoir for its cooling and production processes. The effluent management system is crucial for treating wastewater before it is discharged into the Long Sea Outfall (LSO). This system includes five pumping sumps, with No. 2 sump being particularly important for regulatory compliance (Appendix 1). Continuous monitoring of key parameters like temperature, pH, and flow rate is performed using SCADA and IFiX systems, which trigger alarms when these parameters go out of acceptable ranges [3].

However, the current system relies heavily on manual monitoring. Operators at No. 2 sump often have to check the sump’s status because the existing on/off monitoring system has limitations. This reliance on manual oversight creates operational inefficiencies and raises the risk of equipment failures. As a result, 24-hour staffing is required to maintain compliance and ensure smooth operations. Additionally, alarms are only visible locally at the No. 2 sump, making remote management more challenging.

Figure 1 – Overview of No.2 Sump and LSO

With the ongoing reduction in on-site staff, it’s crucial to ensure that the output and compliance of No. 2 sump are not compromised. Tata Steel has set aside £20,000 to automate the system, allowing operations to run smoothly without the need for constant on-site supervision. By integrating advanced sensors, programmable logic controllers (PLC), and remote monitoring capabilities, this project aims to improve the system's efficiency and sustainability, aligning with Tata Steel’s commitment to environmental responsibility. The general layout of the site and its connection to the Long Sea Outfall (LSO) is shown in Figure 1.

## 1.3 Solution

To keep No. 2 sump operational and compliant despite reduced staffing, the project will implement several key upgrades. A new Allen-Bradley PLC will be installed to improve control capabilities, allowing for remote monitoring and automatic regulation of pump operations [4]. The current Red Lion HMI will remain, but a new screen will be developed for remote control, enabling operators to manage the system from different locations [5].

Integrating with the existing SCADA network will provide real-time data and alarm visibility, so any deviations can be quickly addressed without needing to be physically present at the sump [6]. Enhancements to the Motor Control Centre (MCC) panel will also ensure compliance with HSG253 guidelines for safe equipment isolation during maintenance [7]. By replacing the existing overload protection with Allen-Bradley overloads, it can improve data collection and monitoring, helping operators optimize performance and maintain compliance.

Figure 2 – Graph of Predicted benefits

New level transmitters and float switches will be installed to enhance the accuracy of sump level measurements, increasing the reliability of the pumping system and reducing the need for manual oversight [8]. Together, these upgrades will allow the system to operate efficiently with minimal daily supervision, enabling better use of human resources, figure 2 show some predicted gains. This shift is essential to maintain the compliance and output of No. 2 sump despite ongoing staffing changes.

### 1.3.1 Benefits of the Automation Project

Automating No. 2 sump is crucial for ensuring compliance and operational efficiency during staffing changes. By introducing a PLC-based control system, advanced sensors, and remote monitoring, the project will allow continuous operation without needing on-site personnel [2]. This system will help meet regulatory requirements and significantly cut down on labour needs, as 24-hour staffing will no longer be necessary, only occasional checks by staff will be required.

This modernisation will also boost operational efficiency by reducing downtime and equipment failures while improving monitoring capabilities. Operators will have complete visibility and control from remote locations, allowing for quick responses to alarms. Additionally, better resource allocation and reduced labour costs will support a more sustainable operational model for Tata Steel [9].

## 1.4 Methodology

The project will follow a structured methodology comprising several phases. First, a comprehensive analysis of the current sump management system will identify areas for improvement. Consultation with stakeholders will help align project goals with operational needs. Next, appropriate automation technologies will be researched and procured, particularly focusing on the selection of the Allen-Bradley PLC and associated hardware.

Following this, control logic will be developed, along with new HMI screens, which will then be integrated with SCADA for remote monitoring. The installation of the new PLC, sensors, and MCC panel upgrades will take place next, followed by rigorous testing to ensure that the system operates according to specifications and regulatory standards. Finally, operators will receive training on the new system, ensuring a smooth transition to the automated operations.

## 1.5 Limitations

This project focuses specifically on No. 2 sump and does not extend to other areas of the effluent management system. Mechanical pump modifications will not be included, nor will a comprehensive overhaul of the system. Additionally, while this initiative addresses staffing changes related to No. 2 sump, it does not cover broader implications of staffing adjustments across Tata Steel.

## 1.6 Chapter Summary

The automation of No. 2 sump is vital for maintaining compliance and operational efficiency, particularly in light of reduced staffing levels. By integrating PLC-based control, advanced sensors, and remote monitoring capabilities, this project ensures that operations remain unaffected by staffing changes. Through these enhancements, Tata Steel can uphold its commitment to environmental compliance and operational excellence, setting a precedent for future automation initiatives within the organisation.

# Chapter 2: Research & literature Review

# 2.1 Research & literature Review

Automating effluent systems has become increasingly important in industrial environments, especially where compliance, cost control, and reliability are critical. Across the UK and Europe, industries are under pressure to modernise outdated infrastructure and meet stricter environmental standards. The literature reviewed in this chapter supports the need for smarter monitoring, reduced manual input, and safer control systems. This project applies those principles at Tata Steel, where an older manual sump system was upgraded using modern automation tools.

There is a clear shift across the sector toward automation, with the Environment Agency and Natural Resources Wales (NRW) pushing for greater visibility of site discharge performance [10] [11]. Tata Steel’s upgrade to No. 2 sump reflects this direction automating a legacy asset to align with ISO 14001 and NRW permit BL7108IM requirements.

While most academic and industry literature focuses on greenfield automation projects or large-scale urban systems, there is limited discussion of cost-sensitive retrofit upgrades within existing, heavily regulated industrial infrastructure. This project addresses that gap by showing how a phased automation approach can deliver measurable results within legacy systems, with minimal downtime and disruption to operations.

## 2.2 Automation Technologies in Effluent Management

PLCs are commonly used in effluent control due to their reliability and flexibility in harsh conditions. Ahmed et al. [2] focuses on reducing human error through process automation, Bernabei [12] emphasises the value of modularity and phased upgrades in constrained environments. Together, these perspectives support a control strategy that prioritises both reliability and adaptability key requirements for retrofitting legacy systems like No. 2 sump. The decision to use an Allen-Bradley PLC at Tata Steel is supported by its compatibility with existing site infrastructure and its performance in other high-reliability environments [1] [4].

Adaptive automation is becoming more common in environments where staffing reductions and safety concerns make manual monitoring difficult. Bernabei [12] describes how modular systems allow phased upgrades without the cost of full system replacement. This approach was key at No. 2 sump, where downtime needed to be minimal and panel space was limited.

These insights supported the reuse of the CR3000 HMI already installed on site, which offered protocol flexibility and reduced the need for retraining. This decision reflects Inductive Automation’s HMI design recommendations [5], which emphasise clarity, minimalism, and alignment with operator expectations to reduce error rates during alarm conditions.

## 2.3 Remote Monitoring and Control

Platforms like SCADA and iFIX allow operators to monitor and control systems remotely, which is especially useful when staffing is reduced. Gevernova [3] outlines how remote interfaces improve efficiency by reducing unnecessary checks and improving alarm response. SCADA integration at Tata Steel now allows centralised alarm handling and better shift coordination [6].

As SCADA systems become more connected, security risks increase. Alanazi [13] and Paul [14] both note that unauthorised access is a growing concern in industrial networks. In response, this system was firewalled from external access and locked behind restricted access points aligning with best practice in SCADA security architecture.

Additionally, the HMI was redesigned with user feedback in mind. Following best practice guidance [5], the interface was simplified to include clear pump states, fault indicators, and control toggles. This helped reduce training time and improve user confidence.

## 2.4 Operational Efficiency and Resource Allocation

Manual sump systems require constant monitoring, which uses significant operator hours. Yandan [9] and Yang et al. [15] both highlight that automating basic routines frees staff for more complex or strategic work. This project reduced sump coverage from 168 hours per week to under 20, a shift that supports both cost savings and smarter resource use.

Operational data is now logged through SAP, giving visibility of unplanned faults, backlog jobs, and work orders [16]. These logs help prioritise future maintenance and were used to track project improvements. Kenton [17] supports this data-led approach through Lean Six Sigma, using KPIs and fault trends to drive ongoing process improvements [18].

### 2.4.1 Legislative Compliance Context

In the context of environmental automation at Tata Steel, several regulatory frameworks guided the system's design and implementation. These include:

- Water Resources Act 1990 – governing the discharge of effluent into controlled waters [10].

- Electricity at Work Regulations 1989 – ensuring electrical systems are safely installed and operated [19].

- Health and Safety at Work Act 1974 – covering employer duties to maintain a safe workplace [20].

- Control of Substances Hazardous to Health (COSHH) – ensuring effluent systems do not expose workers to chemical hazards [21].

- Tata Steel EIS 7 (Low Voltage Safety Rules) – providing specific standards for equipment under 1000V AC [22].

These were met by implementing proper lock-off/tag-out procedures, clear MCC panel labelling, and by using a documented isolation process (Appendix 4).

## 2.5 Environmental Compliance

Environmental expectations are tightening across the UK. Pillman [11] and NRW [10] explain that permit conditions now require real-time reporting, not just spot sampling. This is backed by UK-wide strategies for nature recovery and emissions control [23] [24]. At Tata Steel, this means automated systems must ensure that pH, oil, and solids levels never exceed permit thresholds, and alarm before they do [25].

To meet ISO 14001 expectations, this system uses alarm setpoints based on NRW limits. Redundant level transmitters with fault detection logic ensure compliance even if one sensor fails. Data is logged and can be audited, supporting both internal reporting and third-party reviews.

This approach is consistent with national policy, such as the Environment Agency’s digital strategy [23], which promotes SCADA-based systems for improving environmental transparency and long-term monitoring across industrial sites.

## 2.6 Ethics of automation

While automation improves safety and performance, it often impacts manual roles. Tata Steel has pledged to redeploy affected workers, but this is a wider issue across UK industry. Mekid [26] and Ramaswamy [27] argue for ethical frameworks that balance efficiency with retraining and long-term support. Carroll [28] also notes that poor transition planning can lead to inequality and morale issues.

To support operators, this project included dedicated training and a user-led HMI layout. By giving teams input during the design stage and offering documentation during rollout, it aimed to make the transition smoother and more inclusive.

## 2.7 Electrical Compliance and Safety Standards

### 2.7.1 HSG253 – The safe Isolation of Plant and Equipment

Compliance with safety regulations, such as HSG253 “The Safe Isolation of Plant and Equipment” is critical in industrial operations. The literature emphasises that proper isolation procedures are essential for ensuring worker safety and minimizing risks during maintenance and operational interventions. Upgrading the MCC panel buttons to comply with these guidelines is a proactive measure that addresses safety concerns while enhancing operational reliability [7] [20].

### 2.7.2 Tata Steel Low Voltage rules EIS 7

Tata UK’s Low Voltage Safety Rules serve as a practical application of the EAWR, specifically for equipment operating below 1000V AC and 1500V DC. These rules not only reinforce the regulations but also draw from real-world incidents and best practices in the industry [22]. The incorporation of standards such as BS 7671 and HSG85 ensures that Tata UK’s approach aligns with recognised safety practices. The Low Voltage Safety Rules outline essential safety measures, including restricted access to high-risk areas and the proper installation of barriers. These protocols are supported by research indicating that clear safety measures significantly reduce the risk of electrical accidents. Furthermore, the requirement for visible emergency procedures and adequate workplace organisation enhances readiness for potential incidents [22].

### 2.7.3 IEC 61131 Standard

IEC 61131 is a key standard in industrial automation, establishing a solid framework for programmable controllers. It facilitates interoperability, streamlines complexity, and increases productivity, greatly shaping the design and execution of automation systems. To fully capitalize on its benefits, ongoing training and the integration of new technologies are vital. Future initiatives should aim to address implementation hurdles and ensure that the standard keeps pace with advancements in the industry [29].

### 2.7.4 Machine Safety Standards

In addition to UK-specific regulations, the system design also aligns with relevant international standards including EN ISO 12100 [30] for machine safety principles, EN ISO 13857 for operator access protection, and EN 60204-1 [31] for electrical equipment safety. While the system does not require a SIL-rated safety controller, principles from EN ISO 13849 [32] and DIN EN ISO 13849-1 [32] were considered when evaluating control reliability, fault handling, and the use of redundancy in transmitter selection logic.

## 2.8 Technology Selection Justification & Integration Strategy

When selecting technologies for effluent automation, key factors include system reliability, ease of integration, vendor support, and long-term maintainability. The literature suggests that automation solutions are most effective when components are compatible with existing infrastructure and when support is available for configuration, updates, and operator training [2] [12].

Programmable Logic Controllers (PLCs) remain the foundation of most industrial automation systems. Muthukrishnan [1] notes that Allen-Bradley PLCs are widely used in high-reliability environments due to their proven stability and strong vendor ecosystem. These PLCs support Ethernet/IP protocols, enabling seamless communication with smart relays, HMIs, and SCADA platforms [4].

Human-Machine Interfaces (HMIs) play a crucial role in making automated systems operable by technicians and operators. Inductive Automation [5] highlights the importance of intuitive layouts, colour-coded alarm states, and responsive controls in improving usability and reducing training time. Devices that support multiple communication protocols, like Modbus TCP and EtherNet/IP, are especially useful in mixed vendor environments.

Smart motor protection relays, such as the E300, are often used to improve visibility of equipment status. These devices allow monitoring of voltage, current, and thermal load, feeding critical data to SCADA systems. RS [4] reports that their integration can simplify diagnostics, reduce wiring complexity, and support predictive maintenance strategies.

The integration of these technologies should also consider network security. As Alanazi et al. [13] explains, SCADA systems are increasingly exposed to cybersecurity threats. Segregating networks, using access control measures, and configuring firewalls are recommended practices when linking PLCs and HMIs to wider plant systems.

Overall, literature supports a selection strategy that balances cost with technical performance and vendor support. By choosing scalable, interoperable technologies that comply with recognised standards such as IEC 61131 [29], organisations can future-proof their systems while meeting immediate operational and compliance [6]

## 2.9 Chapter Summary

This review confirms that the approach taken at Tata Steel is in line with modern automation practices and regulatory expectations. Key findings include:

- Technical Benefits: PLCs and smart relays reduce error and improve safety [6] [4] [12].

- Remote Access: SCADA improves visibility and supports leaner operations [3] [6].

- Environmental Compliance: Real-time monitoring supports ISO 14001 and NRW [25] [10].

- Industry Trends: Reflects a wider UK push toward automation and energy control [33] [23].

- Ethical Focus: Worker impact must be considered with training and feedback [26] [27] [28].

- Data-Driven: SAP logs and KPIs support long-term process improvement [16] [18].

In short, this project applies proven automation methods to a brownfield site, modernising its operation while keeping compliance, safety, and sustainability at the core of its design.

In summary, Tata Steel’s automation upgrades enhance operational efficiency, safety, and compliance. By embracing advanced technologies and safety standards, the company is well-prepared for organizational restructuring and future growth in a rapidly evolving industrial landscape.

# Chapter 3: Research, development & Methodology

# 3.1 Research, development & Methodology

This section outlines the structured process used to automate Tata Steel's No. 2 sump effluent management system. The goal was to enhance reliability, ensure environmental compliance, and reduce manual workload using industry-recognised tools such as PLCs, SCADA systems, and structured programming environments like Studio 5000 [34].

In addition, this project will leverage Lean Six Sigma principles to enhance overall performance while reducing manpower requirements. Lean Six Sigma focuses on process improvement and waste reduction, providing a framework for continuous improvement [17]. By applying these principles, it can systematically identify inefficiencies in the current processes and streamline operations, ensuring that the automated system not only meets regulatory standards but also operates at optimal efficiency.

Training programs will prepare operators to manage the new systems effectively, promoting continuous improvement and collaboration with industry experts. This roadmap is essential for achieving a sustainable solution for Tata Steel’s effluent management needs.

## 3.2 Development & Methodology

### 3.2.1 Feasibility Assessment

- Specific: Conduct a technical feasibility study to assess the Allen-Bradley PLC's compatibility with existing systems [4].

- Measurable: Document findings in a report covering at least three compatibility factors (e.g., communication protocols)

- Achievable: Use in-house engineering resources for the assessment.

- Relevant: Ensures the PLC functions effectively within the current infrastructure

- Time-bound: Complete within four weeks.

### 3.2.2 Technology Assessment

- Specific: Evaluate two PLC options and two types of advanced sensors for sump level monitoring.

- Measurable: Create a comparative matrix outlining key features and costs for each option.

- Achievable: Collaborate with technology vendors for demonstrations

- Relevant: Identifying the right technology is crucial for efficiency and compliance.

- Time-bound: Complete within six weeks.

### 3.2.3 System Design

- Specific: Design a PLC control system for No. 2 sump automation, including a remote monitoring interface.

- Measurable: Develop and test at least one prototype design based on user requirements.

- Achievable: Utilise engineering teams and software tools for design.

- Relevant: A functional design is essential for automation goals.

- Time-bound: Finalise within eight weeks.

### 3.2.4 Integration and Commissioning

- Specific: Develop an integration plan for the PLC with existing SCADA and HMI systems [6].

- Measurable: Aim for a successful integration test with at least 80% data accuracy

- Achievable: Use internal IT resources for implementation

- Relevant: Ensures systems work cohesively for effective monitoring

- Time-bound: Complete within six weeks after the design phase.

### 3.2.5 Training and Knowledge Transfer

- Specific: Develop a training program for operators on the new PLC and monitoring system

- Measurable: Train the five remaining operators and assess their competency post-training

- Achievable: Use internal and external resources as needed

- Relevant: Ensures staff can operate the new system efficiently

- Time-bound: Complete within three weeks post-pilot testing.

### 3.2.6 Regulatory Compliance and Environmental Impact

- Specific: Conduct a compliance audit against Natural Resources Wales regulations [10].

- Measurable: Identify and address compliance gaps in at least one key area.

- Achievable: Involve environmental compliance specialists.

- Relevant: Maintaining compliance is critical for operational legitimacy.

- Time-bound: Complete within four weeks.

### 3.2.7 Lean Six Sigma Implementation

- Define: Identify the key processes involved in the current manual operations and establish baseline performance metrics.

- Measure: Use data collection methods to quantify current inefficiencies and pinpoint areas for improvement. (SAP) [16].

- Analyse: Utilise statistical tools to analyse process performance and identify root causes of inefficiencies.

- Improve: Develop solutions to optimize the automated system and reduce waste, including streamlining workflows and enhancing system responsiveness.

- Control: Establish control measures and KPIs to ensure continuous monitoring and adherence to the new processes, promoting ongoing improvement [18].

## 3.3 Data Collection

This project will use a dual-source approach for data collection to capture a full picture of operational activity. The main system is SAP, Tata Steel’s integrated management tool for planning, tracking, and documenting work in real time [16]. It supports performance monitoring and decision-making across maintenance and operations.

Alongside SAP, operators will maintain a logbook to record any tasks not logged digitally. This ensures no significant activity is missed and provides a more complete operational overview [16].

Key data from SAP will include:

- Time Spent on Tasks – to analyse productivity and workflow efficiency

- Tasks Completed per Operator – to assess workload, set benchmarks, and identify training needs

- Task Type and Complexity – helping to allocate resources and plan future skill development

- Faults and Breakdowns – used to identify patterns and guide preventative maintenance

- Contractor Work and Costs – for budget tracking and justification of outsourcing

- Work Backlogs – to prioritise resources and identify delays

- Planned Work – supporting scheduling and long-term planning

Figure 3 – SAP maintenance log

This structured approach will provide a reliable performance baseline, support continuous improvement, and ensure operational visibility throughout the automation project. Example of the information that will be used to collect data from SAP is in Figure 3 below.

## 3.4 Project Planning

Based on the research, development, and methodology established in earlier stages, a detailed Gantt chart was created to guide the execution of the No. 2 Sump Upgrade project. This chart provided a strategic framework by visually mapping the timeline, phases, and milestones, allowing the project team to manage priorities, allocate resources effectively, and monitor progress throughout the implementation. [35].

The Gantt chart (Figure 4) outlined each phase from initial scoping and stakeholder engagement to final commissioning and handover using clear task dependencies and durations [35]. Key milestones included PLC panel fabrication, phased pump upgrades, and SCADA commissioning. These helped ensure alignment with operational needs and compliance requirements, while facilitating communication across engineering, operations, and environmental teams [36].

To ensure minimal disruption to site functionality, the upgrade was carried out in a phased manner. This guaranteed that a minimum of four pumps remained in operation at all times. The planned approach included:

- Prefabrication of the PLC control panel

- Sequential re-wiring and commissioning of individual pumps

- Verification of both manual and automatic operation modes before advancing

This modular strategy reduced the risk of effluent breach during high-flow conditions and allowed commissioning to pause and resume without affecting baseline operations.

Figure 4 – Gant chart before changes

However, due to unforeseen circumstances including resource constraints and parallel site works the original plan was condensed. Certain wiring and testing stages were merged, while others were accelerated by reallocating engineering hours. Stakeholder consultations were held to communicate these changes and obtain formal approval for the revised schedule.

Figure 5 presents the updated Gantt chart, reflecting changes made to ensure delivery within the new timeframe while maintaining safety and procedural integrity.

Figure 5 – Gantt change after changes

To further support clarity and execution, a summary of major milestones is provided in Table 1:

Table 1 – Gantt Chart summary

By leveraging this structured planning methodology, it work successfully navigated complex integration tasks, maintained compliance with safety/environmental standards, and delivered a robust automation solution for effluent discharge control.

## 3.5 Components selection

The bill of materials is located in appendix 3, this has the full list of materials used and cost.

### 3.5.1 PLC Selection

The Allen-Bradley E300 was chosen because it’s already a standard motor protection device at Tata Steel and works directly with the existing PLC and SCADA systems on site. It connects over EtherNet/IP and integrates easily into Studio 5000, which made setup quicker and simpler. The E300 handles all the key protection features like overloads, phase loss, and motor jams without needing extra relays or wiring. Using it also helped reduce the amount of programming needed in the main PLC, since diagnostics and control can be handled within the E300 itself. Overall, it made sense to stick with a proven and familiar device that fits into the plant’s current setup. Table 2 was used to compare different Allen Bradley PLC before a final chose was made.

Table 2 - PLC Selection

| Feature / Spec | E300 (Smart Relay) | Micro850 (Compact PLC) | ControlLogix 5580 (High-End PLC) |
| --- | --- | --- | --- |
| Device Type | Smart motor protection relay (not a full PLC) | Small standalone PLC | Modular high-performance PLC |
| Power Supply | 24V DC or 120/240V AC | 24V DC | 24V DC or via rack |
| Expandable / Modular | I/O, EtherNet/IP module option | Up to 4 expansion I/O modules | Fully modular (chassis-based) |
| EtherNet/IP Support | Native support | Native support | Native support (multiple ports) |
| Current Draw | ~150–200 mA @ 24V DC | ~190–220 mA @ 24V DC | ~250–300 mA per module |
| Communication Rate | 100 Mbps (EtherNet/IP) | 100 Mbps | 1 Gbps (ControlLogix 5580 models) |
| Memory / Processing Power | Minimal – for device-level logic | 64 KB program, 20 KB data | Up to 40 MB program, 3 GB user memory |
| Studio 5000 Integration | Full Add-On Profile | Requires Connected Components Workbench | Seamless with Logix/Studio 5000 |
| HMI/SCADA Compatibility | FactoryTalk passthrough | Supports basic HMI integration | Advanced SCADA & analytics capability |
| Application Suitability | Motor control and monitoring only | Small machine control / standalone apps | Complex process automation / enterprise systems |
| Use at Tata Steel | Yes – standard for motor protection | Rarely used | Yes – standard for major plant systems |
| Device Type | Smart motor protection relay (not a full PLC) | Small standalone PLC | Modular high-performance PLC |
| Power Supply | 24V DC or 120/240V AC | 24V DC | 24V DC or via rack |
| Expandable / Modular | I/O, EtherNet/IP module option | Up to 4 expansion I/O modules | Fully modular (chassis-based) |
| EtherNet/IP Support | Native support | Native support | Native support (multiple ports) |
| Current Draw | ~150–200 mA @ 24V DC | ~190–220 mA @ 24V DC | ~250–300 mA per module |
| Communication Rate | 100 Mbps (EtherNet/IP) | 100 Mbps | 1 Gbps (ControlLogix 5580 models) |
| Memory / Processing Power | Minimal – for device-level logic | 64 KB program, 20 KB data | Up to 40 MB program, 3 GB user memory |
| Studio 5000 Integration | Full Add-On Profile | Requires Connected Components Workbench | Seamless with Logix/Studio 5000 |

### 3.5.2 HMI Selection

The Red Lion CR300007 was chosen because it offers excellent flexibility and supports a wide range of industrial protocols, including Modbus TCP and EtherNet/IP, which makes it compatible with both Rockwell and non-Rockwell systems. Its built-in web server and data logging features were also key benefits, allowing operators to access system information remotely and store operational data without needing a separate SCADA system. The device’s ability to handle multiple protocols at once made it ideal for this project, where integration with different devices and future expansion were important factors. In addition, its rugged IP66-rated front panel and broad temperature range made it well suited for harsh industrial environments like those at Tata Steel. Table 3 was used to choose the selected HMI.

Table 3 – HMI Selection

| Feature / Specification | Red Lion CR300007 | Allen-Bradley PanelView Plus 7 700 | Siemens SIMATIC HMI KTP700 Basic |
| --- | --- | --- | --- |
| Display Size & Type | 7" Widescreen TFT LCD, 16M colours | 7" TFT LCD, 65K colours | 7" TFT LCD, 256 colours |
| Resolution | 800 x 480 pixels | 800 x 480 pixels | 800 x 480 pixels |
| Touchscreen | Resistive analog | Analog resistive | Resistive |
| Ethernet Ports | 2 x 10/100Base-T(X) | 1 x 10/100Base-T | 1 x 10/100Base-T |
| Serial Ports | 2 x RS-232, 2 x RS-232/RS-485 | None | 1 x RS-485 |
| USB Ports | 2 x USB Host, 1 x USB Device | 1 x USB Host, 1 x USB Device | 1 x USB Host, 1 x USB Device |
| Expansion Capabilities | Expansion port for modules | None | None |
| Protocol Support | Over 300 protocols; multi-protocol support | EtherNet/IP, DF1, DH-485 | PROFINET, MPI, PROFIBUS DP |
| Data Logging & Web Server | Yes | No | No |
| Power Supply | 10–30 VDC | 18–30 VDC | 24 VDC |
| Operating Temperature Range | -10°C to 50°C | 0°C to 55°C | 0°C to 50°C |
| Environmental Ratings | NEMA 4X/IP66 front panel | NEMA 4X/IP66 front panel | IP65 front panel |
| Configuration Software | Crimson 3.1 | FactoryTalk View Studio | WinCC Basic |
| Notable Features | Web server, SD card, modular expansion | Rockwell integration, prebuilt templates | Basic control, Siemens integration |
| Typical Applications | Complex, multi-protocol integration | Standard HMI in Rockwell environments | Simple applications in Siemens setups |

### 3.5.3 Cable Selection

The project required a range of cabling solutions to support control signals and power distribution between panels and field devices. A 10-pair screened cable was used for internal panel signal wiring, while a 19-core 1.5 mm² SWA (Steel Wire Armoured) cable was selected for interconnecting the network panel with the pump control panel. This ensured both sufficient core count and mechanical protection suitable for the site’s industrial environment. Tri-rated 18 AWG (0.75 mm²) cable was used for internal panel terminations, offering flexibility and compliance with electrical panel standards. Glands, heat shrink, and general cable management accessories were also used to ensure a safe, tidy, and professional installation.

### 3.5.4 Control Panel Components

A range of standard panel components were used in the build, including relays, terminal blocks, DIN rail, and trunking. Schneider and Finder relays were selected based on reliability and availability, while modular terminal blocks ensured neat and serviceable wiring layouts. Accessories such as ferrules, grommet strips, and cable markers supported a clear and maintainable design. All components were chosen to match existing Tata Steel specifications, ensuring standardisation and compatibility across site installations.

### 3.5.5 Tools & Installation Aids

General installation accessories such as Wago lever terminals, 3M double-sided tape, and heat shrink tubing were used to support fast and clean installation work. These resources helped with temporary test setups, cable dressing, and mounting of components within the panel. Small but essential consumables were pre-packaged for use on-site to reduce installation time and improve efficiency during shutdown periods.

### 3.5.6 Safety & Labelling

To comply with electrical safety and site identification standards, cable labels, warning tags, and panel markings were applied throughout the build. These labels ensure that operators and maintenance staff can easily trace and identify connections during servicing or fault diagnosis. Proper labelling also contributes to site audit compliance and reduces risk during isolation procedures [22].

### 3.5.7 Sensors

Ultrasonic level transmitters were chosen for monitoring the No. 2 sump due to their non-contact design, reliability, and proven performance in effluent environments. They’re already used across site, which made them a sensible and supported option.

A dual setup was used to add redundancy. The PLC uses a custom AOI to compare readings, ignore any failed signal, and alarm when needed. This ensures the pumps keep running even if one transmitter fails.

The approach follows guidance from EN ISO 13849 [32] and HSG253 [7], both of which support fault-tolerant input systems for safety-critical control. It also helps reduce unnecessary stoppages and improves system uptime.

Sensor choice and logic were reviewed with site engineers to make sure they match existing maintenance procedures and spare part availability.

Two configurations were reviewed during design a primary/fallback setup and a voting logic setup. The second was selected for its improved reliability and full-time monitoring.

# Chapter 4: Design and implementation

## 4.1 Design and implementation

### 4.1.1 Overview of Key Hardware

The upgraded system is built around a CompactLogix PLC platform, integrated with a Red Lion CR3000 HMI, ultrasonic level transmitters, and a hardwired float switch. The PLC and HMI are housed in a dedicated control panel located in the MCC room. Two ultrasonic sensors provide redundant level measurement, while a float switch offers a failsafe condition in the event of transmitter failure. A breakdown of this is shown in table 4.

Table 4 - Overview of components

### 4.1.2 PLC and Panel Installation

The CompactLogix PLC and CR3000 HMI were installed within an existing enclosure located in the MCC room. The enclosure was modified to meet EIS 7 and HSG253 standards, with the addition of clear labelling, updated E-stop wiring, and re-routed internal wiring for safety and accessibility. Ethernet communications were routed via a dedicated internal switch, and power supplies were protected with DIN-rail mounted breakers.

### 4.1.3 Field Instrumentation

Field instruments include two ultrasonic level sensors mounted above the sump. These provide real-time level data to the PLC via 4-20mA signals. A float switch is mounted at the high-level point and wired directly to a digital input as a secondary failsafe. All field cabling is routed through flexible conduit to junction boxes near the pump area.

### 4.1.4 Communication and Integration

Figure 6 – iFIX Effluent screen

The system communicates over EtherNet/IP, linking the PLC, E300 motor relay, and HMI. The HMI and PLC are configured with static IPs and securely routed to the site’s SCADA network (iFIX). The dual ultrasonic level transmitters are processed using voting logic within the PLC, ensuring that invalid or flatlined readings are excluded from control decisions. An example of this is in Figure 6.

## 4.2 Safety Considerations

The most important consideration is the safety of personnel carrying out any task. To ensure this, several safety measures must be followed. Below are the steps taken to maintain safety.

### 4.2.1 Electrical isolation

Following the EIS Low Voltage Safety Rules and HSG253 safe isolation of equipment, all isolation points must have a lock attached [22]. After isolation is completed, a safety document is filled out and given to the team. This document was used to safely carry out the work on the MCC pump panels at No. 2 sump. The isolation procedure and certificate are located in Appendix 3 [7]. This will then be put in permit office Figure 7.

Figure 7 – Isolation process

### 4.2.2 Control safety

To ensure a safe system of work, a fail-safe design is necessary. This guarantees that in the event of a fault, the system will automatically shut down in a way that won’t affect other systems or personnel. In this project, the ultimate stop floats prevent damage to the pumps. Emergency stop buttons on the MCC pump panels ensure that the pumps can be stopped immediately in an emergency. Alarm systems also play an important role, and it’s critical that they are reliable and have redundancy built in.

### 4.2.3 Personnel safety

There are several safety considerations to keep in mind before, during, and after the work is completed. The correct personal protective equipment (PPE) must be worn throughout the task to protect personnel as much as reasonably possible. Ensuring safe access to and from the MCC panels and removing obstacles like doors to prevent manual handling risks, is important. Uneven ground is another hazard that could cause injury. After the work is finished, documentation and commissioning tests should be completed. Training must be provided to all personnel working in the area.

### 4.2.4 Environmental

Spill kits must be available in every area to handle substances that could harm the environment. Given the environmental risks at No. 2 sump, a COSHH risk assessment must be carried out before using any substances that could be hazardous [21].

### 4.2.5 Management of change

Management of Change (MoC) is essential for ensuring that changes do not lead to unintended consequences. While change brings risks, effective management can reduce them [37]. A solid MoC process facilitates planning, implementing, and managing changes to prevent impacts on worker safety, public health, the environment, assets, and customer deliverables.

The MoC framework captures changes, identifies risks, and assesses their effects on areas like procedures and training [37]. It also outlines work plans for safe implementation, engages stakeholders, secures approvals, and updates documentation. This structured approach minimizes risks to acceptable levels.

Improperly managed changes can significantly increase risks to personnel safety, environmental integrity, security, reliability, and product quality.

A thorough risk assessment is crucial. Before implementing any change, it is vital to evaluate the associated risks and ensure that necessary precautions are taken to mitigate them.

### 4.2.6 Testing of system

Once the installation was complete, several rounds of testing were carried out to ensure all components functioned correctly and safely. Each pump was tested individually in both manual and automatic modes using the new PLC and HMI interfaces. The level control logic was verified by simulating different sump levels and confirming the correct sequence of pump activation and deactivation.

The system’s response to faults was also tested. This included triggering the ultimate stop float to confirm that all pumps would shut down and require manual reset, as well as simulating transmitter failures to check if alarms were raised and logic switched to the secondary transmitter. Timeout and interlock logic were validated to ensure pumps would not restart prematurely or under unsafe conditions.

Testing also involved remote access checks through SCADA. Operators were able to view alarms and sump levels in real-time, and manual override functions were confirmed to be working correctly. All tests were logged and reviewed before sign-off.

### 4.2.7 Documentation and training

A set of user-focused documentation was developed to support ongoing operation and maintenance of the system. This included:

- A simplified overview of the PLC logic structure

- HMI screen descriptions and manual/auto mode instructions

- Safety procedures, including fault reset protocols and E-stop locations

- Wiring diagrams and MCC panel layouts

- Troubleshooting tips for common alarms or faults

This documentation was made available in both digital and printed formats at the control room.

For training, operators were given a walkthrough of the new system, with an emphasis on key differences from the manual setup. The training covered how to use the HMI to start/stop pumps, interpret alarms, and reset faults. One-on-one sessions were conducted during shift handovers to make sure each operator had hands-on experience.

Feedback from operators during training was used to improve the clarity of the HMI and supporting documents. Future recommendations include creating a short refresher guide and incorporating training into onboarding for new staff. Training hand-over records and operator guidance materials are included in Appendix 8.

### 4.2.8 Installation & Commissioning Task Summary

The commissioning process followed a structured risk-controlled approach. Each task was clearly documented with specific mitigations. By combining physical safety measures (e.g. signage and guarding) and software controls (e.g. level checks, ultimate stop, and rollback options), the transition to the new control system was executed with minimal disruption and in full compliance with site safety standards. Table 5 below shows the main tasks, in appendix 2 the full table of risks are detailed.

Table 5 – Risk Assessment break down

## 4.2 Implementation

Figure 8 is a single line diagram (SLD) providing an overview of the proposed plan, helping to understand the system layout.

Figure 8 – SLD of plan

### 4.2.1 Pump panel installation

The first step of the implementation involved performing an isolation. Once completed, an electrical permit to work was issued, allowing the work to begin. The old isolator and overload were removed, followed by the installation of the new Allen Bradley E3000. This process included removing the old bus bars, auxiliary wires, and backplate. With all the old equipment cleared, the new components were installed. The images below showcase the before and after stages of the work. The internal panel layout and external wiring modifications are shown in Appendices 5 and 6.

Figure 9 – Before and after for panel internal controls and power controls

The panel installation involved reorganizing the auxiliary wiring to enhance accessibility for future maintenance and troubleshooting. This change ensures that technicians can perform tasks more efficiently, reducing downtime during repairs or upgrades. The cables were properly dressed and secured using cable ties and wire ducts to create a clean, organised, and professional appearance, minimising clutter and potential wiring hazards.

The installation for one pump was successfully completed over six days. This included configuring a new button layout on the panel door for improved operator usability, with careful attention to ergonomics and functionality. Additionally, all associated wiring was routed and connected to match the new design, ensuring reliable operation and compliance with electrical standards. Comprehensive testing was also performed to verify the integrity of connections and the correct operation of all components. More images are in appendix 7.

Figure 10 – Panel Final Layout After Refurbishment

### 4.2.3 PLC network set up and Coding

The Allen Bradley PLC was programmed using Studio 5000 Logix Designer. To simplify the design and implementation process, the code was organised into sections. Custom instructions, known as add-ons (AOI), were utilised to contain complex logic for reuse within the main program. This approach enhances the readability of the main program and significantly reduces its overall size [34]. A full ladder diagram of this logic is available in Appendix 4 for reference.

### 4.2.4 AOI Available Pump Counter

The Available Pump Counter utilizes a function block implemented in Structured Text (ST), which is reflected in the main program. The AvailPumpsCounter(Figure 11) logic is designed to count the available pumps in the system based on their individual availability statuses. This structure clearly illustrates the input/output relationships, effectively demonstrating how the program assesses the operational capacity of the pump system.

Figure 11 - AOI – Available Pump Counter Overview Diagram

In this PLC program (figure 12), tags are categorized into Inputs and Outputs, with two primary data types utilized: BOOL and DINT.

BOOL (Boolean): This data type is used for binary states, typically representing on/off, true/false, or yes/no conditions.

DINT (Double Integer): This data type is used for storing integer values that can range from -2,147,483,648 to 2,147,483,647, allowing for the representation of larger numerical values, such as counts or measurements.

Figure 12 - ST Code Structure for Pump Availability Logic

For this part of the code, structured test (ST) was used. The reason for this is to make it easier as an AOI when checking availability of five pumps and counts how many of them are available. The ST code is shown below and broken down (Figure 13).

Figure 13 ST Code

Availability array

Step one to five is an array named ‘Avail’ this is being populated with the availability status of five pumps (P1_Availability, P2_Availability, P3_Availability, P4_Availability, and P5_Availability) (figure 14).

Each element in the Avail array corresponds to whether a particular pump is available or not (usually a Boolean value, TRUE or FALSE).

Figure 14 - Pump Availability Logic Loop Initialization

Loop through pumps (figure 15)

Step number seven uses ‘FOR’ loop iterates over the indices of the Avail array from 0 to 4. This means the loop will run five times (for each pump).

Figure 15 - Counting Available Pumps Using FOR Loop

PumpCountTemp (figure 16)

Step 8 to 10 initialised to 0. This variable will be used to count how many pumps are available.

Figure 16 - Increment Pump Count on Availability Check

Count Available Pumps (figure 17)

The code checks if the pump at the current index (iC1) is available by evaluating Avail[iC1]. If the pump is available (TRUE), it increments PumpCountTemp by 1.

Figure 17 - Loop Termination and Count Finalization

End of Loop (figure 18)

Step 14 is the end of the inner IF statement and continues to the next iteration of the loop.

Figure 18 - Output Assignment for Available Pumps Count

Store Count (figure 19)

Step 16 is after the loop has finished executing, the total count of available pumps is stored in the variable Pumps Available.

Figure 19 - Final Pump Availability Output Mapping

### 4.2.5 AOI Dual Transmitter Selector

Figure 20 – Dual Transmitter AOI overview

Tag list of inputs and outputs

Figure 21 below shows the inputs and outputs used in the dual transmitter select function block and the data types are shown (BOOL, REAL).

Figure 21 - Dual Transmitter Selection – Tag List Overview

Figure 22 - Transmitter 1 Manual Selection Logic

Line 0 (figure 22) – handles the manual selection of Transmitter 1. The operator can select a transmitter using HMI_TransmitterSelectManual, which is a manual input from the HMI. The system will then compare the values of the two transmitters and select Transmitter 1 if its scaled value is greater than or equal to Transmitter 2’s, and if there are no faults in Transmitter 1.

Line 1 (figure 23)– This rung mirrors the logic of Rung 0 but handles the manual selection of Transmitter 2. The system will compare the two transmitter values and select Transmitter 2 if its scaled value is greater than or equal to Transmitter 1’s, and if there are no faults in Transmitter 2.

Figure 23 - Transmitter 2 Manual Selection Logic

Figure 24 - Dual Transmitter Fault Alarm Logic

Line 2 (figure 24)– This rung manages the alarm and reset logic for dual transmitter faults. If both transmitters (Transmitter 1 and Transmitter 2) have faults, the system triggers an alarm. Additionally, a reset condition is managed from the HMI using HMI_BothLevelTxFaulted_Reset.

Figure 25 - Dual Transmitter Fault Reset from HMI

Line 3 (figure 25) - This rung further handles fault reset logic, specifically providing the HMI interface for resetting the dual transmitter fault condition. It provides a simple mechanism for operators to manually reset the faulted condition.

Line 4 (Figure 26) – This rung handles the manual swapping of transmitters using HMI_ManualSwapTransmitters. The operator can manually select between Transmitter 1 and Transmitter 2, regardless of their values or fault conditions.

Figure 26 - E300 Interface – Relay Ladder Integration

### 4.2.6 AOI E300 Interface

The E300 motor management relay provides key monitoring and control functions for motor applications. The images highlight the integration of this device in both relay ladder logic and function block diagrams within a control system, typically implemented in industrial automation software.

Relay Ladder Integration:

The ladder logic view of the E300_Interface shows a set of parameters related to motor health and performance being interfaced with the relay. These parameters include:

- FLA_Percentage: Full Load Amperes percentage, indicating motor load.

- TCU_Percentage: Thermal Capacity Utilization, measuring thermal load on the motor.

- Current Monitoring: L1, L2, and L3 currents.

- Voltage Monitoring: L1-L2, L2-L3, and L3-L1 voltages.

- Power Metrics: Real Power, Apparent Power, and Power Factor.

This ladder logic interface appears to enable monitoring of these parameters, although actual data values are not shown in the provided logic, indicated by the placeholder? symbols.

Function Block Diagram Integration:

The function block diagram (FBD) also presents the E300_Interface with similar parameters as the ladder logic but formatted in a modular block that integrates the motor relay's input/output points. The diagram allows easier manipulation of the motor's data for processing in more complex control schemes. Each output is labeled for clarity and is tied to corresponding outputs:

- E300: Primary relay interface for motor monitoring.

- FLA_Percentage, TCU_Percentage, L1_Current, L2_Current, L3_Current: Motor operating parameters.

- Voltage readings: Phase-to-phase voltage monitoring (L1L2, L2L3, L3L1).

- Power Parameters: RealPower, ApparentPower, ReactivePower, and PowerFactor.

Figure 27 - E300 Interface – Function Block Diagram

Figure 28 below provides the detailed mapping of the E300_Interface’s data points. Each parameter is listed alongside its corresponding data type (e.g., REAL for numerical values) and its role as either an input or output to the system.

Figure 28 - E300 Interface – Tag mapping

Figure 29 - E300 Scaling ladder logic

This ladder logic (figure 29 shows how the values from the E300 relay (such as FLA percentage, currents, voltages, and power metrics) are processed through SCL (Scaling) blocks before being output as engineering values. Scaling ensures the raw data from the E300 relay is converted into usable units that match the control system’s needs.

Figure 30 below shows ladder logic specifically for voltage monitoring. The voltages between L1L2, L2L3 and L3L1 are input into the scaling blocks before being output as values.

Figure 30 - E300 Voltage monitoring logic

### 4.2.7 AOI Pump Manager

Figure 31 - AOI Pump Manager – Relay Ladder Diagram

The relay ladder diagram (figure 31) that outlines several components related to the operation of the pump system. The pump manager manages these elements by receiving inputs signals and determining appropriate outputs, such as whether the pump is available, in fault or queued for operation.

Figure 32 below represents a function block that is used for pump management, the function black structure included various inputs and outputs representing different statuses, controls and fault conditions. This is a different vision of the relay ladder.

Figure 32 - AOI Pump Manager – Function Block Diagram

The figure (33) below shows the tags, data type, inputs and outputs.

Figure 33 - Pump fault and timer preset logic

Figure 34 - Overload fault detection

Section 1 Line 0 to 4 (figure 24) – These lines initialising timer presets for various faults and operations, the timers are set of the main contactor faults, overload faults, and fault resets operations.  The fault rest logic (OSR/OSF) are one-shot rising OSR and on-shot failing OSF instructions ensures that the faults reset only occurs for one scan when triggered.

Section 2 line 5 to 10  (figure 35) – section 2 is used to detect an overload condition, where both hardwired and PLC signals are checked. When a fault occurs, it triggers the rest mechanisms and sets fault flags to be cleared. The managed delays related to closing and opening of the main contractor. If the main contactor doesn’t operate within a preset time, a fault flag is set. And the system enters fault mode.

Figure 35 - Contactor fault logic

Figure 36 - Manual/Remote mode logic

Section 2 Line 11 to 15 (figure 36) – This section detects faults ( overload, relay faults, etc.) and if any of these are true, an overall fault flag is set. This flag is used to stop or manage further operations. Checks for external AOI timeouts for pump operations. If any timeout conditions are true, the timeout active bit is energised.  When the pump has a run request active but is queued or timed out, the logic energises the pump Queued flag to manage the sequence in which the pump runs.

Section 4 line 16 to 18 (figure 37)– This section checks whether the system is in manual mode (HMI) or remote mode (MCC panel) based on various switch states. Depending on the mode, the control logic will behave differently.

Figure 37 - Interlock and availability logic

Figure 38 - Start/Stop relay logic

Section 4 line 19 to 22 (figure 38) – Interlocks and availability logic checks whether interlocks are healthy, for example emergency stop relay, float switch relay, etc.. if these are healthy, the system sets the PLC_LcksHealthy bit and allows the pump to start. Based on the interlock and man/auto mode, these lines set bits that define whether the pump is available for operation in automatic or manual mode. This controls if the pump if ready to run.

Section 4 line 23 to 26 (figure 39) – Start/Stop commands, If the pump is available and the auto-run request is active (or manual start is triggered from HMI), the Run Request flag is set, which enables the pump to start. Start Relay Control logic ensures that the PLC_CloseStartRelay closes only when the start pulse is true. It uses timers and reset instructions to manage when the relay should open or close.

Figure 39 - Timeout logic initiation

Figure 40 - Final timeout reset logic

Section 4 line 27 to 30 (figure 40)- Timeout Initiation when the mains contactor is closed and other conditions are met, the timeout logic is initiated to prevent immediate re-starts or consecutive failures. Timeout Reset happens Once a timeout period has elapsed using timers like Tmr_RepTimeout, the system resets the timeout flag to allow the pump to reattempt operation or prevent further faults.

Figure 41 - Scaling block example with mA signal conversion

Section 3 line 31 to 33 (figure 41) - Final Timeout is when the final rung ensures that after the timeout has been processed and the delay has elapsed, the system resets any flags, ensuring the pump is ready for future operations. The program then ends.

### 4.2.8 A – Scaling

In this ladder logic diagram (figure 42), the scaling blocks (SCL) are used to convert the raw 4-20 mA analog signals from various transmitters (level and pH) into corresponding process values. These values are then converted into a percentage of the sump height, where 4 mA corresponds to 0% (an empty sump) and 20 mA corresponds to 100% (a full sump). In the diagram shown, a current of 13.416 mA is scaled to represent 58.85% of the sump height.

Figure 42 - Duty shift priority logic

### 4.2.9 B – Pump Selection

The Pump selection is using ladder logic to duty shift the five pumps. It starts by initialising pump priorities, then when the duty shift is triggered, it temporarily stores the current priorities, updated them according to the new shift, and finally, assigns the pumps to various stages based on the availability and priority. The program also ensures the process only occurs once per duty shift request using one-shift rising instructions.

Figure 43 - Duty shift temporary storage

Line 0 (figure 43) – scans and initialises default priorities for the five pumps P1 – P5 by using MOV (Move) instructions. A priority of 1 – 5 is sent.

Figure 44 - Duty shift priority application

Line 1 (figure 44) – once triggered duty shift one-shot rising (OSR) instruction is used, it will activate a temporary duty shift bit (DutyShift_OB) which activate the program, ensuring the duty shift process only runs once.

Figure 45 - Priority transfer logic

Line 2 (figure 45) – Once the duty shift one shot bit is activated, this section of logic stores the current priorities of pumps (selector_P1_Pri to Selector_P5-Pri) into a temporary array (TempPriArray[0] to TempPriArray[4]). This prepares for shifting or rearranging the priorities.

Figure 46 - AOI Pump selection logic

Line 3 (figure 46)– After the priorities are stored, the priorities are transferred back to the pump selector register (selector_P1_Pri to Selector_P5_Pri). Implementing the priority shift.

Figure 47 - Dual transmitter selection AOI

Line 4 (figure 47)– the logic calls a custom add-on instruction (AOI) pump selection. This priorities and assigns pumps to different stages. This ensures the pumps activated based on availability and priority.

Figure 48 – End of ladder

The program is then ended (figure 48).

### 4.2.10 C – Level Control

Figure 49 - Range and bandwidth calc logic

Section 1 Level transmitter AOI (figure 49) – This section manages the selection between two level transmitters to ensure the systems uses the most accurate and reliable reading. The function of the logic is to automatically selects the highest value between two transmitters unless one is in fault.

Figure 50 - Start/stop level setting for pumps

Section 2 Initialise values (figure 50) – This section sets critical parameters that define the operational boundaries of the pump system. the function is to initialise MaxOpLevel, MinOpLevel and UltStopLevel. This is to pick the operational level of minimum, maximum and ultimate stop level.

Section 3 Rang and bandwidth calculations (figure 51) – This section calculates the operational ranges and bandwidth for starting and stopping pumps based on available pump capacity. The function calculated (OpRange) by subtracting the MinOpLevel from MaxOpLevel, this gives a range where the pumps should operate. The OpRange is then divided by the number of available pumps to determine the StartBandwidth, which is the difference in level required for subsequent pumps to start.

Figure 51- Bandwidth assignment per pump stage

Section 4 Setting Start / Stop Level for each stage (figure 52) – This section set specific start stop levels for each pump stage based on the level of liquid in the system. Each pump stage, representing each pump, the logic sets start levels based on the calculated bandwidth. The first starts at the MinOpLevel, and subsequent stages start at intervals defined by the StartBandwidth. Each stage is also assigned stop levels calculated from StopBandwidth, ensuring pumps turn off as the level drops. The fewer pumps are available, the start point for higher stages is set to a value.

Figure 52 - Stage running check logic

Section 4.1 Stage Running Check (figure 53) – This section checks whether a specific stage is running based on conditions of the pump and the corresponding level. The logic uses comparisons between the stage numbers and associated pump statuses to determine if a pump is currently running. When a pump is running at a given stage, the StagePumpRunning output is activated, signalling the system and operators about the pump’s status.

Figure 53 - Pump sequencing with delay

Section 5 Automatic sequencing (figure 54) – This section introduces timed delays between stages to ensure pumps start in sequence without overwhelming the system. The timers are used to delay the starting of each stage by 20 seconds (using TON – Timer on delay). This prevents multiple pumps from starting at the same time, which could cause electrical or mechanical stress on the system. The timers ensure smooth, staggered operation across all stages.

Figure 54 - Stage delay implementation

Section 5.1 Issuing run requests – This sections sends automatic run requests to each pump when system conditions are met. Once a pump is queued and ready to run, the PumpAutoRun Request is sent to the corresponding pump. This ensures that the pump only run when needed, based on the liquid level and stage conditions. Each pump is tied to specific stage, and the logic ensures that the correct pump is activated for each stage.

Section 6 Pump Level Mapping for HMI (figure 55)– This section ensures the pump start/stop levels are visible on the HMI for operators to monitor. The start and stop levels for each pump stage are written to specific variables using MOV (Move) instructions. These variables are then displayed on the HMI, allowing operators to monitor real-time conditions for each stage. It gives the operators a clear view of the current levels and pump activity, improving system oversight.

Figure 55 - Pump level mapping for HMI

Spanning Multiple sections – Stage start/stop conditions span across multiple sections, these define when each pump stage should start and stop, based on the systems current liquid level. The logic compares the current level from the level transmitter to predefined start/stop levels for each pump. If the current level exceeds the start level for a stage, the corresponding pump starts (using GRT – Greater than instructions). Each stage has its own start/stop conditions based on the level control.

### 4.2.11 D – Pump Management

In pump management, each pump is broken down into each pump 0 – 4.  Each AOI will manage the status and control of multiple pumps in a system. Each pump manger block handles various inputs and outputs related to specific pumps, such as faults. There are timeouts for time limits before an action is taken, and a local or remote control.

There is also a E300 interface, for the interface for monitoring electrical parameters of pumps, example the in-line voltages or current (figure 56).

Figure 56 - Start/Stop span logic across levels

### 4.2.12 Main Routine

The ladder logic below (figure 57) shows multiple jump to subroutine (JRS) instructions. Each JSR bock refers to a specific subroutine by name, these reference the code that has previously been shown. These types of logic ensure that the program jumps to these subroutines to execute specific tasks at the specified points in the sequence.

Figure 57 - Main Routine – JSR call logic

Firmware Checks

The purpose of the firmware checks are used to store and calculate the complete firmware version of the controller for use in SCADA. It then can be used for monitoring, troubleshooting and documentation purposes (figure 58).

Figure 58 - Firmware checks for SCADA

### 4.2.13 HMI

To reduce cost, the existing Red Lion CR3000 HMI was retained, but the interface and programming were completely overhauled to support the new PLC logic. The goal was to provide clear visibility and intuitive control for both local and remote operation.

The design process followed several key steps:

- Tagging and Signal Planning: Tags were mapped and reviewed before programming began to ensure alignment with SCADA and PLC logic (Figure 59).

Figure 59 - Tag List Developed Prior to HMI Programming

Figure 60 - Initial Mock-up of HMI Layout

Mock-up and Iteration: An initial screen layout was drafted using Crimson 3.1 software (Figure 60), which was reviewed and revised based on operator feedback (Figure 61).

Figure 61 - Refined HMI Layout Concept

- Layout Optimisation: The final design features dedicated pump status indicators, manual/auto toggles, and level visuals. Icons and colours were chosen to match existing SCADA conventions, reducing training time (Figure 62 & 63).

Figure 62 - Finalised HMI Interface Deployed to Panel

Figure 63 - Final HMI Testing with Revised Pump Icons

Key HMI design considerations:

- Usability: The interface prioritises readability and simplicity. Only essential controls are shown on the main screen to reduce clutter and avoid mis-operation.

- Operator Feedback: Tag assignments and page layouts were refined based on input from site staff during shift handovers. This helped reduce resistance to the changeover.

- Testing: The interface was validated alongside PLC commissioning to confirm alarm responses, level feedback, and manual control functionality. Operators confirmed that fault resets, mode switching, and pump control behaved as expected during trials (Figure 64).

Figure 64 - Final Programming View with Crimson Software

This HMI redesign supports seamless local operation and prepares the system for full SCADA integration, aligning with the site's future digitalisation goals.

# Chapter 5 – Evaluation

## 5.1 System Testing and Results

Once the new system was installed, several tests were carried out to make sure everything worked as expected. The PLC controlled the pumps properly and kept the sump level within the set limits. The sequencing logic prevented too many pumps from starting at once, and the timeout settings worked to avoid overheating.

Remote access through SCADA also worked well. Alarms triggered when tested and live monitor levels without needing to be on site, which was one of the main goals of the project.

## 5.2 Efficiency Gains

Before this project, the sump had to be manned 24/7. Since commissioning, that’s dropped to around 2/3 hours of operator time per day, just for checks and basic maintenance. That’s a big improvement and frees up operators for other tasks.

## 5.3 Compliance and Safety

There have been no compliance issues since the change. The new system detects faults and safely shuts down pumps using the ultimate stop float. It’s a solid backup and adds peace of mind.

## 5.4 Issues Faced

There were a few hiccups mainly with the HMI scaling at the start. Some of the alarms were triggering too early due to mismatched values between the HMI and PLC. The scaling logic was adjusted to sort this. Also, training the operators took a bit longer than expected, mostly getting used to the new control layout and remote functions.

## 5.5 Operational Metrics from SAP

The table below presents a comparison of key performance metrics collected from SAP logs and operational records before and after the automation of No. 2 sump. The results clearly indicate improvements in labour efficiency, fault reduction, and system reliability.

Table 6 – Operator improvement

These figures highlight a dramatic reduction in operator time, from full 24/7 coverage to an average of just 18 hours per week. Pump faults and manual interventions fell by over 80%, reflecting improved system reliability. Additionally, the reduced need for external contractor support and a decline in work order backlog indicate better resource utilisation. The automation of No. 2 sump has clearly delivered tangible operational benefits that align with the project's objectives of efficiency, compliance, and sustainability.

The SAP system played a crucial role not only in post-installation analysis but also in supporting decisions throughout the commissioning process. Data on fault frequency, maintenance logs, and unplanned downtime was used to:

- Prioritise which pumps were rewired first

- Justify the inclusion of ultimate stop float switches

- Quantify the return on investment in terms of reduced operator workload and labour callouts

By baselining metrics before implementation and comparing them at each milestone, the project team was able to iteratively improve response times and adjust training content. This data-centric approach was consistent with Lean Six Sigma principles adopted during planning.

# Chapter 6 – Conclusion

The automation of No. 2 sump has delivered measurable improvements in operational efficiency, reliability, and regulatory compliance. By replacing manual control with a PLC-based system and SCADA integration, Tata Steel has achieved a robust, low-maintenance solution that reduces labour demands without compromising performance.

The successful implementation confirms that similar legacy systems across the plant can benefit from automation, especially as staffing resources are restructured. The project has proven that digital transformation can coexist with stringent safety and environmental requirements when executed with clear planning and stakeholder involvement.

The project successfully delivered the automated upgrade within the allocated £20,000 budget, despite component cost fluctuations. The final system not only met technical expectations but also achieved measurable operational savings and reduced environmental risk. Budget adherence, alongside enhanced diagnostic capabilities, has laid the foundation for further rollouts across similar sites at Tata Steel. Supporting documentation, including full risk assessments, wiring diagrams, and HMI configurations, are provided in the appendices at the end of this report.

Recommendations

- Consider rolling this setup out to the other sumps, starting with the ones that are still manually controlled.

- Look into adding predictive maintenance in the future using SCADA trends to spot faults before they cause downtime.

- Make sure any future updates include time for proper training, especially when changing how things are controlled.

- Get regular feedback from operators so the system stays user-friendly and efficient.

# Chapter 7 Reflection

This project has been a great learning experience. It was the first time I took a system all the way from design through to testing and implementation. Working on a live site came with challenges especially around safety and documentation but it also made the project feel real and worthwhile.

I learned a lot about PLC programming, HMI design, and how to think ahead when it comes to fault handling and safety. I also saw just how important it is to communicate with end users the operators to make sure what I design actually works for them.

Looking back, I’m proud of how far the project came. It gave me confidence working with industrial systems and helped me understand how automation can be used to solve practical problems not just in theory, but on the shop floor.

Throughout the project, several key lessons stood out:

- Plan for operator feedback early – Getting operator input during the HMI design phase helped avoid confusion later. If repeated, I’d include a feedback loop before finalising the interface.

- Test alarm scaling thoroughly – Initial issues with HMI scaling caused incorrect alarm triggering. Next time, I’d validate alarm thresholds earlier during simulation or bench testing.

- Expect delays and adjust plans – Due to site constraints, some wiring stages had to be merged. A more flexible Gantt plan with built-in buffer time would have reduced pressure during commissioning.

- Balance documentation with usability – Some early documentation was too technical for end-users. In future, I’d create two versions: one for engineers and one simplified version for operators.

These takeaways will inform future automation work and support smoother rollouts in similar environments.

# Chapter 8 References

| [1] | V. Muthukrishnan, “https://www.electrical4u.com,” 15 02 2025. [Online]. Available: https://www.electrical4u.com/programmable-logic-controllers/. [Accessed 15 02 2025]. |
| --- | --- |
| [2] | F. J. D. H. R. H. N. Ahmed, “Barriers to Innovation in Water Treatment,” Water MDPI, vol. 15(733), no. 11, p. 11, 2023. |
| [3] | Gevernova, “https://www.gevernova.com,” 2020. [Online]. Available: https://www.gevernova.com/software/documentation/ifix/version61/pdf/Understanding%20iFIX.pdf#:~:text=iFIX%C2%AE%20is%20a%20Windows-based%20HMI%2FSCADA%20component%20of%20the,inter-operability%20between%20your%20plant%20floor%20and%20business%20systems.. [Accessed 16 02 2025]. |
| [4] | RS, “https://uk.rs-online.com,” 11 02 2025. [Online]. Available: https://uk.rs-online.com/web/b/allen-bradley?cm_mmc=UK-PPC-DS3A-_-bing-_-2_UK_EN_Allen%20Bradley_Phrase-_-Allen%20Bradley_Pure-_-allen%20bradley&gclid=c96750550c5c1fc0784f37a07b0751b1&gclsrc=3p.ds&kwd-72018709348204%3Aloc-188=&matchtype=p&msclkid=c9675055. [Accessed 11 02 2025]. |
| [5] | inductiveautomation, “https://inductiveautomation.com,” 10 02 2025. [Online]. Available: https://inductiveautomation.com/resources/article/what-is-hmi. [Accessed 10 02 2025]. |
| [6] | V. Muthukrishnan, “SCADA System: What is it? (Supervisory Control and Data Acquisition),” 16 06 2024. [Online]. Available: https://www.electrical4u.com/scada-system/. [Accessed 20 02 2025]. |
| [7] | HSE, “The safe isolation of plant and equipment,” HSE, 2006. [Online]. Available: https://www.hse.gov.uk/pubns/books/hsg253.htm. [Accessed 30 10 2024]. |
| [8] | Vacuum Level Limited , “https://pvl.co.uk,” 22 08 2024. [Online]. Available: https://pvl.co.uk/blogs/blog/understanding-the-difference-between-float-switches-and-level-switches. [Accessed 16 02 2025]. |
| [9] | W. Yandan, “Digital transformation, resource allocation, and operational,” International Journal of Research Studies in Management, vol. 12, no. 9, pp. 146-156, 2024. |
| [10] | NRW, “Natural Resourses Wales,” 13 05 2020. [Online]. Available: https://naturalresources.wales/permits-and-permissions/permit-applications-consultations-and-decisions/final-permit-decisions-for-sites-under-industrial-emissions-directive/south-west-wales/tata-steel-uk-limited-v15/?lang=en. [Accessed 30 10 2024]. |
| [11] | C. Pillman, “Regulating the water industry: Why we will always prioritise the best outcome for Wales’s environment,” 31 01 2024. [Online]. Available: https://naturalresources.wales/about-us/news-and-blogs/blogs/regulating-the-water-industry-why-we-will-always-prioritise-the-best-outcome-for-wales-s-environment/?lang=en. [Accessed 01 11 2024]. |
| [12] | M. C. F. Bernabei, “Adaptive automation: Status of research and future challenges,” Robotics and Computer-Integrated Manufacturing, vol. 88, no. 102724, 2024. |
| [13] | M. M. A. C. M. Alanazi, “SCADA vulnerabilities and attacks: A review of the state‐of‐the‐art and open issues,” Computers & Security, vol. 125, no. 103028, 2023. |
| [14] | K. Y. G. Paul, “Architecture and security of SCADA systems: A review,” International Journal of Critical Infrastructure Protection, vol. 34, no. 100433, 2021. |
| [15] | T. Y. X. L. S. C. T. Yang, “Intelligent Manufacturing for the Process Industry Driven by Industrial Artificial Intelligence,” Engineering, vol. 7, no. 9, pp. 1224-1230, 2021. |
| [16] | SAP, “https://www.sap.com,” 20 02 2025. [Online]. Available: https://www.sap.com/about/what-is-sap.html. [Accessed 20 02 2025]. |
| [17] | W. S. A. Kenton, “Lean Six Sigma: Definition, Principles, and Benefits,” 01 07 2024. [Online]. Available: https://www.investopedia.com/terms/l/lean-six-sigma.asp. [Accessed 05 11 2024]. |
| [18] | D. Poleski, “https://www.klipfolio.com,” 05 03 2025. [Online]. Available: https://www.klipfolio.com/blog/kpi-importance. [Accessed 15 03 2025]. |
| [19] | HSE, “The Electricity at Work Regulations 1989,” 10 2015. [Online]. Available: https://www.hse.gov.uk/pubns/books/hsr25.htm. [Accessed 01 02 2025]. |
| [20] | HSE, “Health and Safety at Work etc Act 1974,” 15 10 2024. [Online]. Available: https://www.hse.gov.uk/legislation/hswa.htm. [Accessed 15 10 2024]. |
| [21] | Health and Safety Executive, “https://www.hse.gov.uk/coshh/basics/index.htm,” 19 02 2025. [Online]. Available: https://www.hse.gov.uk/coshh/basics/index.htm. [Accessed 19 02 2025]. |
| [22] | Tata Steel Electrical Commitee, Low Voltage Safety Rules EIS 7, Port Talbot : Tata Steel UK , 2024. |
| [23] | GOV.uk, “https://environmentagency.blog.gov.uk,” 11 11 2022. [Online]. Available: https://environmentagency.blog.gov.uk/2022/11/11/reducing-energy-use-and-carbon-emissions-from-pumping/. [Accessed 14 02 2025]. |
| [24] | C. Anothy, “Nature Restoration and Collaboration: Integration and Participation in England’s Local Nature Recovery Strategy Framework,” Journal of Environmental Law, vol. 6, 2025. |
| [25] | TSUK, ISO 14001_Effluent Discharge from Abbey Beach Outfall, Port Talbot: TSUK, 2023. |
| [26] | S. O. H. Mekid, “The blended future of automation and AI: Examining some long-term societal and ethical impact features,” Elsevier, vol. 73, no. 102232, 05 2023. |
| [27] | S. P. J. H. Dr Ramaswamy, “Springer Handbook of Automation,” in Automation and Ethics, New York, Springer, 2023, pp. 809-833. |
| [28] | J. K. Carroll, AI and Ethics, Springer, 2024. |
| [29] | IEC, “International Standards,” 2003-05. [Online]. Available: https://plcopen.org/sites/default/files/downloads/iec_61131-1_preview.pdf. [Accessed 11 12 2024]. |
| [30] | ISO, ISO 12100:2010, ISO, 2022. |
| [31] | I. E. Commission, IEC 60204-1, International Standard, 2016. |
| [32] | ISO, ISO 13849-1:2023, nternational Standard published, 2023. |
| [33] | GOV, “https://www.gov.uk,” 1 04 2025. [Online]. Available: https://www.gov.uk/government/publications/evaluation-of-the-compliant-environment-interim-report/evaluation-of-the-compliant-environment-interim-report. [Accessed 10 04 2025]. |
| [34] | Phantom, “https://vohauipr.com,” 03 12 2024. [Online]. Available: https://vohauipr.com/studio-5000-software-everything-you-need-to-know-and-how-to-get-started/. [Accessed 01 02 2025]. |
| [35] | C. W. R. Shwete Bottorff, What Is A Gantt Chart? The Ultimate Guide, Forbes, 2024. |
| [36] | D. Ramos, “https://www.smartsheet.com,” 03 05 2021. [Online]. Available: https://www.smartsheet.com/content/gantt-chart-pros-cons. [Accessed 19 02 2025]. |
| [37] | L. Altomonte, “Management of Change,” Safety Culture , 2025. |
| [38] | “Automation technologies and their impact on employment: A review, synthesis and future research agenda,” Technological Forecasting and Social Change, vol. 191, no. 21, 2023. |
| [39] | W. Kenton, “https://www.investopedia.com,” 01 07 2024. [Online]. Available: https://www.investopedia.com/terms/l/lean-six-sigma.asp. [Accessed 12 02 2025]. |
| [40] | W. Joy-Amacho, “Opportunities and limitations to environmental management system (EMS) implementation in UK small and medium enterprises (SMEs) – A systematic review,” Journal of Environmental Management, vol. 367, no. 121749, 2024. |

# Appendices

Figure 65 - Sump layout

Appendix 1 – Sump Layout

## Appendix 2 – Risk Assessment

Figure 66 - Project Risk Assessment

## Appendix 3 – Bill of Materials

Figure 67 - Bill of Materials

## Appendix 4 – Isolation Procedure

Isolation Procedure

Summary

Description

Isolation of Pump 3 at No.2 Effluent Sump Pumphouse.

Location

No.2 Effluent Pumphouse

Variation Approval

Standard Procedure.

Marked-up Drawing Reference(s)

16/BJ/GC - 1 16/BJ/GC – 2 7110.55.25.12.003

Suitable Work Scopes

- Pump 3 MCC Panel Control Circuit Overhaul/Rewire - Pump 3 MCC Panel Overload Replacement - Pump 3 Pump Guard Removal to enable instrumentation installation.

Created By :- Scott Thomas

Validated By :- Simon L Jones, John Reed, Rob Price

Definitions

Contingency measures – consideration must be given to a potential for failure during placement or service. These must be put into place before work can commence.

Plant status – what condition the system must be before an isolation can commence.

Precaution – A measure required for safe working secured with a lock and tagged with a danger label.

Instatement -  ‘To put or place in a certain state or position’ This is what steps need to be take to carry out an isolation.

Reinstatement – This to restore the asset in its normal operating position after work has been carried out.

Location of work area

No.2 Effluent Sump Pumphouse is located in the green box. Use designated roadways (follow red arrows) and park in the designated parking area (Red Box).

Access the pumphouse from the parking area by walking along the green arrows, to the pumproom door.

Marked-up Drawings

1

2

3

4

5

Contingency Measures

| Contingency Summary |  |
| --- | --- |
| Action | Measure |
| 1 | 4 other Pumps are available. |

Energy Plant Status

| Item | Description | Confirmation |
| --- | --- | --- |
| 1 | No3 pump Isolator Closed |  |
| 2 | No3 Pump Inlet Isolation Valve Open |  |
| 3 | No3 Pump Outlet Isolation Valve Open |  |

Non-Energy Plant Status

Example

| Item | Description | Confirmation |
| --- | --- | --- |
| 1 | N/A |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |

| Step Number | Precaution Number | Location and Identity of Switch | Operation | Final Status | Confirmation |
| --- | --- | --- | --- | --- | --- |
| 1 |  | MCC Room – Pump 3 MCC Cabinet - Fused Isolator -(3FS) | Open Isolator | Open |  |
| 2 | 1 | MCC Room – Pump 3 MCC Cabinet - Fused Isolator -(3FS) | Lock off and danger label attached to isolator | Isolated |  |
| 3 |  | MCC Room – Pump 3 MCC Cabinet | Test for dead on Load Side of Isolator 3FS | Confirm |  |
| 4 |  | MCC Room – Pump 3 MCC Cabinet | Remove Fuses from Isolator Fuse Carrier | Confirm |  |
| 5 | 2 | MCC Room - Pump 3 MCC Panel - Control Circuit Fuse (F3) | Remove Red Spot Fuse carrier F3, Lock off and danger label attached to fuse carrier lock off device. | Isolated |  |
| 6 | 3 | MCC Room - Pump 3 MCC Panel - Neutral Link (L3) | Remove Red Spot Link L3, Lock off and danger label attached to fuse carrier lock off device. | Isolated |  |
| 7 |  | MCC Room - Pump 3 MCC Panel - Control Circuit Fuse (F3) and Neutral Link (L3) | Test for dead on load side of F3 and L3. | Confirm |  |
| 8 |  | Pumproom – Pump 3 –Inlet Isolation Valve. | Close Inlet Isolation Valve | Closed |  |
| 9 | 4 | Pumproom – Pump 3 –Inlet Isolation Valve. | Lock off and danger label attached. | Isolated |  |
| 10 |  | Pumproom – Pump 3 –Outlet Isolation Valve. | Close Outlet Isolation Valve | Closed |  |
| 11 | 5 | Pumproom – Pump 3 –Outlet Isolation Valve. | Lock off and danger label attached. | Isolated |  |
|  |  |  | END |  |  |

Instatement Procedure

Summary of Precautions and Instatement Tests

Summary of Precautions

| Precaution No. | Description | Final Status | Key No. |
| --- | --- | --- | --- |
| 1 | Electrical Isolation Lock on FS3 | Isolated |  |
| 2 | Electrical Isolation Lock on F3 | Isolated |  |
| 3 | Electrical Isolation Lock on L3 | Isolated |  |
| 4 | Fluid Power Isolation Lock on Inlet Isolation Valve | Isolated |  |
| 5 | Fluid Power Isolation Lock on Outlet Isolation Valve | Isolated |  |

Note -	Precautions shall be recorded either via this table (appended to the electrical certificate) or directly on the electrical certificate.

| Final Key Number |  |
| --- | --- |

Instatement Tests

| No. | Type | Test Criteria | Reference / Location | Result/Certificate No. |
| --- | --- | --- | --- | --- |
| 1 | Electrical Test for Dead | Test for dead on Load Side of Isolator 3FS | MCC Room – Pump 3 MCC Cabinet – 3FS |  |
| 1 | Electrical Test for Dead | Test for dead on Load Side of Isolator 3F and 3L. | MCC Room – Pump 3 MCC Cabinet – 3F, 3L |  |

Instatement Confirmation

| Instatement Complete |  |
| --- | --- |
| I hereby declare that the instatement procedure has been completed in full, all precautions have been placed and all required instatement tests have been carried out. |  |
| Signed (Isolation and Immobilisation Authority) | Name in block letters |
| Date | Time |

Further Controls

| No. | Description |
| --- | --- |
| N/A |  |

Note -	All controls shall be recorded on the electrical certificate.

Monitoring and Testing Requirements

| Frequency | Type | Test Criteria | Reference / Location |
| --- | --- | --- | --- |
| N/A |  |  |  |

| Step Number | Precaution Number | Location and Identity of Switch | Operation | Final Status | Confirmation |
| --- | --- | --- | --- | --- | --- |
| 1 | 5 | Pumproom – Pump 3 –Outlet Isolation Valve. | Unlock and remove danger label from valve. | Reinstated |  |
| 2 |  | Pumproom – Pump 3 –Outlet Isolation Valve. | Open Outlet Isolation Valve | Open |  |
| 3 | 4 | Pumproom – Pump 3 –Inlet Isolation Valve. | Unlock and remove danger label from valve. | Reinstated |  |
| 4 |  | Pumproom – Pump 3 –Inlet Isolation Valve. | Open Inlet Isolation Valve | Open |  |
| 5 |  | MCC Room - Pump 3 MCC Panel - Control Circuit Fuse (F3) and Neutral Link (L3) | Test for dead on load side of F3 and L3. | Confirm |  |
| 6 | 3 | MCC Room - Pump 3 MCC Panel - Neutral Link (L3) | Replace Red Spot Link L3, Remove Lock, lock off device and danger label from fuse carrier. | Reinstated |  |
| 7 | 2 | MCC Room - Pump 3 MCC Panel - Control Circuit Fuse (F3) | Replace Red Spot Link F3, Remove Lock, lock off device and danger label from fuse carrier. | Reinstated |  |
| 8 |  | MCC Room – Pump 3 MCC Cabinet | Test for dead on Load Side of Isolator 3FS | Confirm |  |
| 9 |  | MCC Room – Pump 3 MCC Cabinet | Replace Fuses from Isolator Fuse Carrier | Confirm |  |
| 10 | 1 | MCC Room – Pump 3 MCC Cabinet - Fused Isolator -(3FS) | Unlock and remove danger label from Isolator. | Reinstated |  |
| 11 |  | MCC Room – Pump 3 MCC Cabinet - Fused Isolator -(3FS) | Close Isolator | Closed |  |
|  |  |  | END |  |  |

Reinstatement Procedure

Reinstatement Testing Requirements Summary

| Type | Reference / Location | Test Criteria | Result / Certificate (C) No. |
| --- | --- | --- | --- |
| Electrical Voltage Test | MCC Room - Pump 3 MCC Panel - Control Circuit Fuse (F3) and Neutral Link (L3) | Test for 110V (AC) on load side of F3 and L3. |  |
| Operational | Check that pump turns on when required in auto and manual. | Pump Turns On |  |

Note -	Where utilised, results shall be recorded either via this table (appended to the electrical certificate) or via a monitoring and testing certificate.

Reinstatement Confirmation

| Instatement Complete |  |
| --- | --- |
| I hereby declare that the reinstatement procedure has been completed in full, the specified plant status has been achieved and all required reinstatement tests have been carried out. |  |
| Signed (Isolation and Immobilisation Authority) | Name in block letters |
| Date | Time |

Figure 68 - Example pump 1 control diagram

Appendix 5 – Single line diagrams

Figure 69 - Example pump 1 diagram continued

Figure 70 - PLC IO

Figure 71 - Pump 1

Figure 72 - PLC Panel

Figure 73 - Panel External Circuits

Figure 74 - Junction Box FLT

Figure 75 - Junction Box INST

Appendix 6 – Data Sheets

Microsoft Word - Document in GPT-020F DS ENG EU 12.2019

Microsoft Word - Scotchfil Electrical Insulation Putty Data Sheet.doc

Microsoft Word - 01771.doc

PowerPoint Presentation

0900766b8157ce52.pdf

A700000008590985.pdf

800F 22 mm Push Buttons

Junior Hacksaw Spare Blades PDF

0900766b813a16e6.pdf

0900766b80020aad.pdf

0900766b816d5135.pdf

0900766b816bcd30.pdf

HellermannTyton Product Catalogue 2016/2017

HT_Product_Catalogue_2019_2020_UK

untitled

0900766b8136ab5e.pdf

0900766b81662473.pdf

Mise en page 1

MicroLogix Programmable Controllers Selection Guide

USB4

0900766b81626d31.pdf

A700000008708095.pdf

PowerPoint Presentation

A700000008880447.pdf

A700000006686053.pdf

A700000006966699.pdf

PowerPoint Presentation

PowerPoint Presentation

A700000008849806.pdf

PowerPoint Presentation

A700000008987707.pdf

A700000008737688.pdf

A700000007530958.pdf

A700000007945282.pdf

PowerPoint Presentation

A700000009342496.pdf

A700000007357530.pdf

A700000007002529.pdf

A700000006950524.pdf

A700000007925596.pdf

A700000007899063.pdf

0900766b8173ef4b.pdf

A700000007945222.pdf

PowerPoint Presentation

A700000008919306.pdf

A700000008971697.pdf

A700000007987644.pdf

A700000008879639.pdf

A700000010954757.pdf

A700000007389514.pdf

Product DataSheet

XALK178F.pdf

XB4BA31.pdf

XB4BA42.pdf

XB4BA21.pdf

XB4BS8444.pdf

XB4BD25.pdf

PIT20B.pdf

Product DataSheet

AZ5DE015.pdf

DZ5CE020.pdf

0900766b80fea980.pdf

3SU1900-0BE31-0AA0

0900766b81395620.pdf

A700000010592812.pdf

A700000009277040.pdf

PDF by Afineo

PNL - Iss H - CHANNEL NUTS

0900766b816b073d.pdf

0900766b810bb197.pdf

0900766b8082679f.pdf

0900766b81241d90.pdf

0900766b8163226e.pdf

0900766b8113a122.pdf

Joker Set of ratcheting combination wrenches SB, 4 pieces

Figure 79a – Before work started

Figure 79b – After work complete and PLC installed

Figure 79c – New cabinet fitted.

Figure 79d – New and existing cables re-glanded, new containment (tray) installed.

Appendix 7 – Images of project

Figure 83a – Before panel wiring upgrade.

Figure 83b – Part way through install.

Figure 83c – Wiring completed; final works ongoing.

Figure 83d – PILZ relay ready to test.

Figure 87a – Plate cut to size and holes in correct location.

Figure 87b – Installed buttons and labels

Figure 87c – ready for wiring.

Figure 87d – Installed face plate under isolation.

Figure 91a – Before upgrade. Old overload and CTs

Figure 91b – After install, new contactor and overload.

Figure 91c – Earth bonding completed

Figure 91d – Bonding & cable protection.

## Appendix 8 – Training and Handover

The following table outlines key training sessions and handover activities carried out from August to November 2024. These sessions involved operations and maintenance personnel and were designed to familiarise them with the upgraded sump automation system, including the PLC, HMI, SCADA integration, and fault handling procedures.

Table 7 – Record of meetings

| Date | Session Type | Personnel Involved | Topics Covered | Feedback / Notes |
| --- | --- | --- | --- | --- |
| 20/08/2024 | Initial Walkthrough | Operator A, Maintenance Tech | System overview, PLC panel layout, E-stops | Good engagement; flagged interest in alarm logic |
| 16/09/2024 | HMI Orientation | Operator B, Technician | Manual/auto control, alarm reset process | Requested clearer screen layout; updated after feedback |
| 17/09/2024 | SCADA Alarm Demo | Day shift ops team | Live alarm test, transmitter fault simulation | Understood alarm triggers and reset |
| 18/09/2024 | Fault Simulation | Technician C, Operator A | Simulated high-level and pump failover | Operator understood reset process |
| 05/10/2024 | Work Instruction Brief | Maintenance Lead | Control logic overview, reset steps | Suggested printed reset procedure at panel |
| 24/10/2024 | Panel Familiarisation | Operators D & E | Wiring layout, fuse access, E-stop use | No issues raised; panel labelled well |
| 20/11/2024 | Final Handover Brief | Supervisor, Maintenance Manager | System sign-off, documentation handover | Signed off with no further changes |
| 28/11/2024 | Operator Feedback Session | Full ops team | Refresher on logic and fault response | Confirmed confidence with new system |