University of Wales Trinity Saint David, School of Engineering

# Heat Exchanger Laboratory Analysis

Thermofluid Mechanics

Bryn Stubbings, 1702064 05/04/2019

Contents

1	Introduction	2

1.1	Heat Exchangers	2

2	Method	3

3	Results	4

3.1	Equations	5

3.1.1	Air Mass Flow Rate	5

3.1.2	Water Mass Flow Rate	5

3.1.3	Specific Heat Capacity	5

3.1.4	Heat Emitted	5

3.1.5	Heat Absorbed	6

3.1.6	Temperature Efficiency	6

3.1.7	Logarithmic Mean Temperature Difference	7

3.1.8	Heat Transfer Coefficient	7

3.2	Final Calculations	8

4	Analysis	9

4.1	Circuit 1	9

4.2	Circuit 2	12

4.3	Circuit 3	15

5	Evaluation	18

6	Conclusion	19

7	Bibliography	21

# Introduction

The experiment carried out to collect results was conducted on 5th March 2019, in a Lab in University of Wales Trinity Saint David’s IQ building. The experiment; carried out by several engineering students, took 100mins to complete. The Experiment involved setting up three different circuits in a heat exchanger and changing one of three parameters; Water flow, Air Flow and Initial Water Temperature.

The machine used for the experiment was a “TD1007 Water to Heat Exchanger” by Tech Equipment. The water element comprised of 2 banks of 16 tube connected in parallel, with the air flowing perpendicular through it. The water was supplied from a heated tank contained in the machine, so the water was recycled after going through the heat exchanger. The machine measured the water and air temperature flowing in and out of the heat exchanger, the flow rate of the water and the pressure difference in the flow of air. The air inlet had a diameter of 100.11mm.

## Heat Exchangers

There are three main types of Heat exchanger; Cross Flow, Counter Flow and Concurrent (parallel) Flow. Cross Flow is where two fluids flow perpendicular to each other, Counter Flow is where two fluids flow in opposite directions to each other and Concurrent is when then flow in the same direction. Heat exchangers are often a hybrid of two or three of these types. The two categories that all heat exchangers will fit into is Recuperative or Regenerative. A recuperative heat exchanger, exchanges heat through a barrier separating the flow of the fluids of which each follow a single path simultaneously. A regenerative heat exchanger has the two fluids using the same flow path alternatively. (Brogan, 2011)

# Method

Before the experiment began the ambient air temperature and pressure for the day and time were noted. In addition, the air inlet orifice diameter, coefficient and the surface area of the Heat exchanger were also noted.

The crossflow heat exchanger was set up with an initial water temperature of 60oc, a water Flow of 2.25l/min and an air pressure difference of 250 pa. The in and out water and air temperatures (TA1, TA2, Tw1, Tw2) were recorded every 4 minutes. After each measurement, the water flow was reduced in increments of 0.5l/min; this was repeated 4 times. For the next circuit the initial water temperature stayed at 60oc, the water flow was set at 0.25l/min, and the air pressure difference stayed at 250pa. The air pressure difference was then reduced in increments of 50 pa every 4 minutes; four times, measurements were taken after each interval. For the final circuit the set up and experiment were the same as the second circuit except the initial water temperature was set to 45oc throughout.

# Results

| Water Flow | Tw1 | Tw2 | ΔTw | Tw Av | Ta1 | Ta2 | Δta | Ta Av |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (L/min) | (°C) | (°C) | (°C) | (°C) | (°C) | (°C) | (°C) | (°C) |
| 2.25 | 61 | 57 | 4 | 59 | 24 | 30 | 5.6 | 27 |
| 1.75 | 61 | 56 | 5.1 | 58 | 24 | 30 | 5.5 | 27 |
| 1.25 | 61 | 54 | 7 | 57 | 24 | 29 | 5.1 | 27 |
| 0.75 | 60 | 50 | 10 | 55 | 24 | 29 | 4.7 | 27 |
| 0.25 | 60 | 38 | 22 | 49 | 24 | 28 | 3.4 | 26 |
| Air Pressure (Pa) |  |  |  |  |  |  |  |  |
| 250 | 60 | 38 | 22 | 49 | 24 | 28 | 3.4 | 26 |
| 200 | 58 | 38 | 20 | 48 | 25 | 28 | 3.2 | 26 |
| 150 | 57 | 38 | 19 | 48 | 25 | 27 | 2.8 | 26 |
| 100 | 57 | 39 | 18 | 48 | 25 | 28 | 3.6 | 27 |
| 50 | 58 | 42 | 16 | 50 | 25 | 29 | 4.3 | 27 |
| Air Pressure (Pa) |  |  |  |  |  |  |  |  |
| 250 | 49 | 34 | 15 | 42 | 25 | 27 | 2.5 | 26 |
| 200 | 48 | 34 | 14 | 41 | 25 | 27 | 2.5 | 26 |
| 150 | 48 | 35 | 14 | 41 | 25 | 27 | 2.5 | 26 |
| 100 | 48 | 35 | 13 | 42 | 25 | 28 | 2.7 | 26 |
| 50 | 49 | 37 | 12 | 43 | 25 | 28 | 3.1 | 27 |

These are the recorded results from the three circuits tested.

After recording the results, a table was created in excel and all the results copied across, this was done so additional values could be worked out easily. The following values were calculated; Air mass flowrate, Water mass flowrate, specific heat capacity at each flow rate, heat emitted, heat absorbed, mean temperature efficiencies, logarithmic mean temperature difference and overall heat transfer coefficient.

Note: the change in temperature for air has been converted in to absolute values for ease of use in portraying the data in graphs.

## Equations

### Air Mass Flow Rate

m=Cd×Ao∆p×2×ρA
m – Air Mass Flow (kg/s)
Cd – Coefficient of Discharge (Orifice) – Value given as 0.6
Ao- Orifice Area (m2)
∆p – Orifice Pressure Drop (Pa)
ρA – Density of Air (Calculated using average air temp and ambient air pressure), (Kg/m3)

### Water Mass Flow Rate

mw=Vf60000×ρw

mw – Water Mass Flow Rate (Kg/s)
Vf – Volume Flow (L/min)
ρw – Water Density (Kg/m3)

### Specific Heat Capacity

#### Water

CpW(at T℃)=CpW(at 15℃)(0.996185+0.0002874T+1001005.26+0.01116×10-0.036T)
CpW – Specific Heat Capacity of Water at Temp, T (J/Kg.K)
T  - Temperature of Water (average temperature used), (oC)

#### Air

As the specific heat capacity of air remains fairly constant for the temperatures the experiment was conducted at, an assumed value of 1005J/Kg.K was used throughout.

### Heat Emitted

QW=mW×CPw×∆TW

QW – Heat Transfer Rate (heat Emitted) of Water (W)
mW – Water Mass Flowrate (Kg/s)
CPw – Specific Heat Capacity of Water (J/Kg.K)
∆TW – Change in Water Temperature (K)

### Heat Absorbed

QA=mA×CpA×∆TA

QA – Heat Transfer Rate (heat absorbed) of Air (W)
mA – Air Mass Flow Rate (Kg/s)
CpA – Specific Heat Capacity (J/Kg.K)
∆TA – Change in Air Temperature (K)

### Temperature Efficiency

#### Water

ηW=TW1-TW2TW1-TA1×100

ηW – Water Temperature Efficiency
TW – Temperature of Water (K)
TA – Temperature of Air (K)

#### Air

ηA=TA2-TA1TW1-TA1×100

ηA – Air Temperature Efficiency
TW – Temperature of Water (K)
TA – Temperature of Air (K)

#### Mean

η=ηW+ηA2

ηA – Water Temperature Efficiency
ηA – Air Temperature Efficiency

### Logarithmic Mean Temperature Difference

LMTD=TW2-TA2-(TW1-TA1)ln(TW2-TA2TW1-TA1)

LMTD – Logarithmic Mean Temperature Difference
TW – Temperature of Water (K)
TA – Temperature of Air (K)

### Heat Transfer Coefficient

U=QWA×LMTD

U – Heat Transfer Coefficient
QW – Heat Energy Transfer Rate (W)
A – Heat Transfer Area (M2)
LMTD – Logarithmic Mean Temperature Difference

Table 2 Initial Results and Final Calculations

Final Calculations

This Table includes the results and calculated values, this table was created in Excel and used to create several graphs for use in comparing the different circuits.

# Analysis

## Circuit 1

Detailed below are the Graphs created from the data shown in Table 2.

Figure 1 Circuit 1 - Heat Exchanged

In Figure 1 the heat absorbed by the air dips off its expected line to below the heat emitted by the water. This happens at the same point that the heat exchanger has the most efficient water mass flow (Figure 2). Due to this and that it does not follow the general trend of the other data point, it has been highlighted as an anomaly in the data. From further analysis of the original data it appears that this may be a result due to the water’s change in temperature being higher than the air’s change in temperature at the peak Heat transfer coefficient (Figure 2).

Figure 2 Circuit 1 - Heat Transfer Coefficient

Figure 2 shows the most efficient point for the heat exchanger is at 0.21kg/s water mass flow. This shows the optimum mass flow for the water at the specific Air Mass Flow (0.114Kg/s). After this point the air is unable to absorb the heat from the water as efficiently so as the water speeds up the passed this point, no enough time is given for the heat to be absorbed by the air.

Figure 3 Circuit 1 - Temperature Efficiency

Figure 3 backs up Figure 2 by showing the temperature efficiencies of the air and water and how they cross over. At the point where they cross over shows that the water has passed its optimum speed and is going too fast to be able to release as much heat as at optimum. The air temperature efficiency does not change much; increasing by about 5% overall, this is because the air mass flow does not change, so changes are mainly influenced by the water mass flow rate.

## Circuit 2

Figure 4 Circuit 2 Heat Exchanged

Figure 4 depicts the heat emitted and absorbed by the water and air as the air mass flow increases. They both follow a similar trend to begin with, then the air heat absorption declines temporarily; similar to the first circuit, this only affects the water heat emission slightly. Both lines then continue upwards with water staying on a similar gradient and air increasing at a greater rate, until air exceeds water. At thus point the water is no longer able to emit its heat energy as fast as the air is able to absorb it.

Figure 5 Circuit 2 - Heat Transfer Coefficient

Unlike Circuit 1 with water mass flow the heat transfer coefficient with air mass flow on circuit 2 appears to continuously increase with a varying gradient. The main fluctuation in the line correlates to the dip in heat absorption on Figure 4. Once again this was treated as an anomaly as it does not follow the expected path.

Figure 6 Circuit 2 - Temperature Efficiency

As a rule, for circuit 2 the water temperature efficiency is increasing, and the air temperature efficiency is decreasing. The air temperature efficiency does however increase slightly, this correlates with Figure 4 and the increased gradient of the air heat absorption.

## Circuit 3

Figure 7 Circuit 3 Heat Exchanged

Similar to Figure 4 both lines crossover at a certain point and the air heat absorption has a sudden increase in gradient whilst the water gradient stays almost the same. The differences are the intersection of the two lines occurs at different points; Circuit 2 (Figure 4) – 0.108Kg/s, Circuit3 (Figure 7) – 0.096. In addition, there is a more noticeable difference in the initial gradients for both lines, Figure 4’s similar initial gradient could be a result of the same error that caused the anomaly.

Figure 8 Circuit 3 - Heat Transfer Coefficient

The heat transfer coefficient in circuit 3 appears more of a uniform curve than circuit 2. The data clearly suggests the coefficient will level off at some point, much like in circuit 1 (Figure 2) and the data collected within a ‘comfort zone’ for the air heat absorption. Unlike circuit 1, in which the water mass flow is the variable, in circuits 2 and 3 the heat transfer coefficient is a constant curve and not a complete straight line.

Figure 9 Circuit 3 - Temperature Efficiency

The temperature efficiency for circuit 3 follows the same general rule as circuit 2 however, with the Lower initial water temperature the efficiency starts slightly higher. The air temperature efficiency remains unaffected by the change. The most noticeable difference between Figure 9 and Figure 6 is the neatness of the lines in Figure 9, this suggests some errors or inaccuracies in circuit 2’s data.

# Evaluation

There are two anomalies in the data, both in circuit one and two and appear to be caused by the same thing. A possible cause for these anomalies may be not allowing enough for the Heat exchanger to reach equilibrium before taking each measurement. The 4minute time lapse used could be extended to 5 minutes. An increase in measurements would also improve accuracy and better highlight anomalies in the data.

The initial water temperature for circuit 3 was consistently 3-4oC above the required temperature. As an improvement to keep the experiment within more acceptable error margins, extra time for the water tank to cool down would be advised. Despite the temperature difference, the temperature fluctuation during the experiment was acceptable.

# Conclusion

Differing characteristics in the 3 circuits can be found in the graphs shown above. In circuit 1 when varying just the water mass flowrate the Emission and absorption rates of the water and air stayed consistent as the mass flowrate increased, with the water heat emission staying consistently below the air heat absorption (negating any anomalies). Whereas, in circuits 2 and 3 when the air mass flow rate was being varied, the air heat absorption rate started well below the water heat emission rate and increased at a higher rate. The two rates intersect at a single point and then continue in previous fashion. This shows that the air heat absorption rate is limited by the flow of water but, will surpass the water heat absorption rate when air mass flow rate is increased. This is reiterated when comparing the heat transfer coefficients. In circuit 1 the heat transfer coefficient increases, peaks, then decreases and starts to level off. Conversely in circuits 2 and 3 the heat transfer coefficient increases at a steady rate the starts to level off towards a peak value. This shows that whilst increasing the water flow too much can have an adverse effect on the performance of the heat exchanger, too much air flow will not.  As a performance enhancement additional banks could be added to the water side to give more time with the water in the air flow, this would increase the optimum water flow at any given air flow.

Figure 10 C2 v C3 Temperature Efficiency

This graph has been constructed to better show the two water temperature efficiencies of circuit 2 and circuit 3; the same experiment with two different starting water temperatures (60oC and 45oC). The anomaly has been removed from circuit 2 to aid in comparison. Circuit 2 with the higher starting water temperature begins with a lower temperature efficiency than circuit 3 but, ends with a higher efficiency. Although only small differences this shows the air heat absorption rate not high enough for the higher temperature of water, however as the air mass flow rate increases the air is able to absorb the addition heat and then exceeds the lower temperatures efficiency. This shows the higher efficiencies possible with higher starting water temperatures when increasing air mass flow. Circuit 1’s temperature efficiency is completely different; showing a drastic drop in water temperature efficiency from over 60% to nearly 10%, finishing under the air temperature efficiency as the water mass flow increases. This show the increase of the water mass flow benefits the air temperature increase slightly, but does not help the water, without increasing the air mass flow.

From this it is clear to see that in order to set up a system with maximum efficiency the water flow must be adjusted to match the air flow. Furthermore, the higher the initial water temperature the higher the air mass flow should be to gain extra efficiency.

# Bibliography

Brogan, R., 2011. Heat Exchangers. [Online] 
Available at: http://www.thermopedia.com/content/832/
[Accessed 04 2019].

Ezgi, C., 2016. Basic Design Methods of the Heat Exchanger. [Online] 
Available at: https://www.intechopen.com/books/heat-exchangers-design-experiment-and-simulation/basic-design-methods-of-heat-exchanger
[Accessed 03 2019].