08/07/2022

Adam Cross (2106959)

Technical report regarding the upgrade of safety critical high-level, guided wave radar instruments on Therminol 3, Stage 1 & 2 Benzene Receiver Vessels

Work Based Project

Contents

2	Abstract	3

3	Introduction	3

3.1	The problem	3

4	Motivation	3

5	Aims & Objectives	3

5.1.1	Aim	3

5.1.2	Objectives	3

6	Legal and Ethical Issues	4

7	Project Planning	4

7.1	Feasibility Studies	4

7.2	Time Constraints	4

7.3	Resources Available	5

7.4	Costs	5

7.5	User Requirement Specification	5

7.6	Product Design Specification (PDS)	5

7.7	Relevant Standards	5

8	Research Method	6

8.1	Background research	6

8.1.1	Guided wave radar level instruments	6

8.1.2	Why guided wave radar?	6

8.1.3	Difference between a Safety Instrumented System (SIS) and a Basic Process Control System (BPCS)?	6

8.1.4	Delta V SIS Instrument Loops	6

8.1.5	What is ATEX?	7

9	Selection	7

9.1	Level Transmitter Character Selection Matrix (CSM)	7

10	Design	8

10.1	Benzene Receiver 18TA0306 AND 18TA0307 Vessels	8

10.1.1	18TA0306 Vessel	8

10.1.2	18TA0307 Vessel	9

11	Implementation	9

12	Testing / Evaluation / Analysis	9

13	Conclusion	10

13.1	Reflection	11

14	References	12

15	Appendices	0

15.1	Research	0

15.1.1	Relevant Standards	0

15.1.2	Level Instrument Quotations	1

15.1.3	Level Instrument Character Selection Matrix	0

15.2	Planning	1

15.2.1	Gantt Chart	1

15.2.2	Feasibility Studies	2

15.2.3	Cost and Time Estimates	5

15.2.4	Tank Dimension Drawings	8

15.2.5	Resources	0

15.2.6	User Requirement Specification	0

15.2.7	Product Design Specification	0

15.2.8	Certificates for Installed Instruments	0

15.2.9	Data Sheet	0

15.3	Implementation	0

15.3.1	Permit to Work	0

15.3.2	CHARM Panel	0

15.3.3	Instruments	1

15.3.4	18TA0306LT20	2

15.3.5	18TA0307LT20	0

15.3.6	Instrument loop drawing	0

15.4	Testing & Reflection	0

15.4.1	Interlock Testing 18TA0306	0

15.4.2	Interlock Testing 18TA0307	6

15.4.3	Final Costs	0

15.4.4	Logbook	0

# Abstract

The purpose of this project is to replace existing SIL1 (safety integrity level) rated guided wave radar instruments 18TA0306LT20 and 18TA0307LT20 on the Benzene Receiver stage 1 and stage 2 vessels at Eastman Chemical Company, Newport’s chemical manufacturing plant Therminol 3 with instruments of a higher safety certification, SIL2 to meet process safety requirements. SIL level instruments are used as a critical safety barrier to prevent overfilling of the vessels containing extremely hazardous Benzene liquid/vapour as well as hydrogen gas that would lead to catastrophic failure of the compressor, potential fire and possible fatality. Thus, the existing VEGAFLEX 81 SIL1 instruments were replaced with SIL2 certified Rosemount 5301 series guided wave radar instruments to increase safety and probability of failure on demand (PFD).

# Introduction

Eastman Chemical Company, based in Newport is a speciality chemical manufacturing plant established in 1949. The key products produced are Therminol and Saflex® (S-2075 plasticizer). The product end uses are photovoltaic heat transfer fluids used in solar electricity plants, and Saflex® in architectural glazing and automotive glazing. The stage 1 and 2 Benzene Receiver vessels belong to a manufacturing plant called Therminol 3 that produces heat transfer fluids. Each vessel has two guided wave radar level instruments, a BPCS (basic process control system) level instrument and a SIL rated safety instrument. The chemical process is run using the BPCS level instrument, the SIL instrument is simply a safety barrier to prevent disastrous consequences.

## The problem

The problem became apparent during a LOPA (Layers of Protection Analysis) review, whereby the SIL1 rating of the existing level instruments and the issue of both vessels containing identical manufacturer devices created some concern, as they placed the LOPA scenarios at the upper end of the PFD scale and as such are among the group of highest process safety risks on the Newport site. It is best practice on chemical processes to use different manufacturer equipment to create diversity and redundancy and as such reduce common failure mode. LOPA is a method used to assess high consequence scenarios to determine if the combination of probability of occurrence and severity of the consequences meet the risk tolerance standard set by Eastman Chemical Company. [1], [2]

# Motivation

The motivation behind this project is clear, as stated in the project proposal document, the level instruments were addressed as being a serious hazard on the Newport site due to their low SIL1 rating and diversity and redundancy issues. The existing level instruments have functioned for many years and never had a problem but there is a higher-than-expected probability that these instruments will fail to operate when needed due to their safety rating. It was therefore important to address the issue as soon as possible. The completed project has improved safety and reliability of the chemical process in terms of PFD and helped to combat the diversity issues that were apparent on the existing system.

# Aims & Objectives

### Aim

The aim of this project is to investigate and rectify non-compliance of two high level safety systems (tags 18TA0306LT20 and 18TA0307LT20) on the 1st and 2nd stage Benzene Receiver vessels of Eastman Chemical Company’s Therminol 3 plant.

### Objectives

By the end of the module (July 2022), the level instruments stated above must be installed and functioning correctly to meet the required safety standards of SIL2 certification to IEC 61508. “Functioning correctly,” means that the instruments must pass the interlock proof tests and must read consistently tracking the original BPCS level reading.

The level instruments must be compatible with the Delta V operating system used at Eastman to control and overlook the chemical process. To be compatible they must utilise the HART 4-20mA communications protocol.

The level instruments must be of the correct size and material for the nature of the process. 18TA0306LT20 probe length must be less than 2644mm but more than 1954mm to measure the full tank range. 18TA0307LT20 probe length must be less than 1950mm but more than 1500mm. While the flange and probe material must be chemical resistant 316/316L steel.

The chosen level instruments must satisfy the ATEX explosive atmosphere rating of the zone, thus must come with an ATEX certification of zone 2G or higher and be an intrinsically safe instrument.

# Legal and Ethical Issues

It is important to address any legal and ethical issues prior to starting the project to outline any potential issues or constraints so that ethical standards are followed.

Some documents and pictures used are Eastman owned and copyrighted; there therefore arises concerns of confidentiality and privacy. It will therefore be important to ensure these documents are stored safely with password protection and handled with care to only be used for the purposes of this University module and are not to be used or shared elsewhere.

(See Appendix 15.1.1), for all relevant legal legislation that this project must abide by in order to be a success. It is vital to work safely at all times adhering to the Health and Safety at Work Act 1974.

It is also crucial to treat all members of the project fairly and with respect so that all parties are happy and working to their best ability.

# Project Planning

## Feasibility Studies

Feasibility studies were carried out on three solutions to help identify and conclude the best possible approach to address the problem. The three manufacturers were chosen due to their reliability shown elsewhere on other plants at Eastman Newport. Each solution was scored on how well it met the set criteria. The minimum required percentage that would suggest a project idea is feasible is 66%. (See Appendix 15.2.2). The solution chosen certainly fits the criteria, it scored the highest feasibility percentage of 92.49%, compared to solution 1 (82.86%) and solution 3 (91.43%).

Solution 1 involved using an Endress + Hauser SIL2 rated level transmitter. It scored highly in most areas but fell short due to a 12-week lead time.

Solution 2 scored highest due to meeting all of the criteria, with a short lead time and the components to help solve the problem permanently.

Solution 3 also scored highly but wasn’t feasible due to the diversity and redundancy constraints explained previously.

## Time Constraints

Many tasks involved in this project will be carried out within working hours, but due to other job roles and responsibilities it may prove difficult to deliver and meet every deadline. It will be important to communicate with E/I Planners and go through the Gantt chart with them to ensure that time is allocated within the workplace maintenance schedule to allow this project to be undertaken.

Timings have been allocated to the costings document (see Appendix 15.2.3). Each task or item that requires time to be allocated to it has been listed under the column “M.H EA,” short for man hours each. It is expected that the implementation stage of this project can be completed in two working days, involving four working parties, mechanical, electrical, DCS (engineer) and scaffolders. All work and tasks prior to this will be completed by DCS and Project Engineers. Again, each task is allocated time, Adam’s time has not been included in the engineering cost estimates as he will be working alongside the Engineers. The implementation of the project has been scheduled during a planned shutdown for week commencing 20th June, as shown in the Gantt chart (see Appendix 15.2.1). A Gantt chart was created to ensure the project ran smoothly by allocating deadlines to specific tasks. Where delays occur, these will be documented on the Gantt chart.

## Resources Available

It was important to create a resources document (see Appendix 1.1.1) to highlight what is available and what is required to carry out this project.

## Costs

The costing document (see Appendix 15.2.3) incorporates all departments and their hourly rates. It is a cost estimate created to allow time to be allocated to each task. The estimated cost of the project is just under the £20,000 budget. This costing document will be amended throughout the project to keep track of actual costs (see Appendix 15.4.3).

## User Requirement Specification

A user requirement specification is a key document that specifies what the level instruments need to be able to do for this project to be a success. This document is used when writing the product design specification, to ensure the needs of the client or end user are met. [3] (See Appendix 15.2.6).

## Product Design Specification (PDS)

The aim of a PDS is to ensure that the final design meets set requirements for it to be a success. The PDS considered a range of requirements such as the performance, compatibility of equipment with existing systems, size requirements and more (see Appendix 15.2.7).

## Relevant Standards

Research was conducted into legislation and standards that were applicable to the project (see Appendix 15.1.1) and that equipment would need to comply to, this also highlighted the importance of health and safety within the project.

# Research Method

The research method for this project will very much involve quantitative analysis in the form of secondary research. Utilising data sheets, journals, and the internet to gather information such as technical specifications and other technical data. These will be used in feasibility studies and character selection matrixes to analyse the gathered data. Some forms of qualitative research will take place when holding meetings with electrical and instrumentation engineers and distributed control systems (DCS) engineers to obtain the knowledge and understanding to undertake the tasks at hand.

## Background research

### Guided wave radar level instruments

A guided wave radar instruments use microwave technology to determine liquid level or distance. Liquid level is calculated using the probe length and distance that the liquid is from the instrument (or tangent line) to provide a liquid level percentage. The distance is calculated by sending low energy guided microwave pulses down a steel rod, when they contact the liquid, they reflect and travel back towards the source (head) of the transmitter, the time it takes for the reflected microwaves to reach the transmitter provides the liquid distance, with the liquid level being directly proportional to the time-domain reflectometry. [4]

Figure 1 [4]

### Why guided wave radar?

In the chemical industry, especially at Eastman, most process conditions inside vessels and tanks vary tremendously, either by a change in temperature, viscosity, or density, which can all cause variations in level measurement. Guided wave radar technology is totally unaffected by these phenomena so does not need to compensate for changes in density, dielectric, or conductivity in the fluid, making it a very robust means of measurement. [4]

### Difference between a Safety Instrumented System (SIS) and a Basic Process Control System (BPCS)?

Safety instrumented systems are extremely important in the functional safety of a chemical processes. A SIS system consists of instrumentation that has a high degree of accuracy and safe failure rate to detect dangerous process conditions and significantly lower the risk of these conditions from becoming a hazard. [5] Whereas a BPCS system is an instrumented system that provides the normal, everyday control and functions of the manufacturing process, without the stringent tolerances to maximise safety. [6]

### Delta V SIS Instrument Loops

The current level system is SIL1 rated, meaning it is rated for the lowest level of SIL safety. The instrument is part of an intrinsically safe, Delta V SIS wiring system, intrinsic safety meaning the wiring out in the field near the instrument is protected by a galvanically isolated, intrinsically safe Zener barrier that prevents a spark with enough energy to cause an explosion, in an explosive atmosphere like the area where the instruments are installed, from forming.

This intrinsically safe barrier is part of the Delta V SIS electronic marshalling unit called a CHARM Smart SIS Logic Solver, shown below in figure 2. This ‘analogue in’ CHARM provides a 24V power supply to the instrument as well as receiving a HART 4-20mA protocol communication to the Delta V operating system over the same cable.[7], [8]

Figure 2 [9]

[9]

Delta V SIS Electronic marshalling is SIL 3-rated and therefore provides the certification to be able to control the lesser rated SIL2 level instruments that will be installed on each of the Benzene receiver vessels with no safety concerns [9]. This means that the existing wiring and input/output CHARM can be used with the new level instruments with no changes required.

### What is ATEX?

ATEX is an explosive atmosphere that can be caused by flammable gases, vapours, or mists. The level instruments are situated in a Zone 1 (2G) ATEX gas zone, this zone has been classified and documented on a drawing by competent personnel. Zone 1 is categorised as an area where there is a likelihood during normal running conditions for there to be an explosive atmosphere present. Thus, the level instruments must be certified to Zone 1 (2G) or greater to comply with the ATEX Directive 99/92/EC and Directive 2014/34/EU). [10]

# Selection

## Level Transmitter Character Selection Matrix (CSM)

Research was conducted into three different brands of level transmitter, Endress+Hauser, Rosemount, and VEGA. (See Appendix 15.1.3). Each device was scored against the criteria taken from the product design specification (see Appendix 15.2.7), scoring from 1 to 5 as shown in the key. This document provided an understanding as to which of the three level instruments would be best suited to the application. The Endress+Hauser device had an overall score of 43 out of 50, it matched the criteria but lead time and price let it down. Next was the VEGA device, again it matched the criteria with a very short lead time, but it scored low in the diversity and redundancy category, although there is no set rule, Eastman prefer to use instruments of different manufacturer as explained previously in the report. Lastly, the winner of the CSM was the Rosemount 5300 series, matching all the specification criteria as well as being the cheapest choice with a short lead time to prevent delays. [11]–[13]

# Design

The instrument drawing (see Appendix 15.3.6) shows that instrument 18TA0306LT20 is connected to CHARM 6 on CSLS321 Baseplate 1, while 18TA0307LT20 is connected to CHARM 7. This is the point of isolation when changing the level instruments and must be removed while disconnecting each device.

## Benzene Receiver 18TA0306 AND 18TA0307 Vessels

The required length of the level probes was established using the vessel schematic diagrams and is listed in the PDS document (see Appendix 15.2.7). The rods/probes must be long enough to measure between the bottom tangent line of the vessel and the top tangent line, shown in figure 3 below.

Figure 3 [3]

Figure 4

Figure 5

18TA0306 Vessel

Figure 6 (see Appendix 16.2.4)

### 18TA0307 Vessel

Figure 7 (see Appendix 16.2.4)

Figure 8

Figure 9

The SIL2 instruments once installed and commissioned must measure the liquid level in the vessel to within 1% of the existing BPCS level instruments and track the level continually and consistently. The trip points and fail modes will be checked during proof testing, as these values will not have changed within the Delta V operating system coding.

# Implementation

Both VEGA instruments were removed from the vessels following a permit to work document being issued by the plant operator. The permit to work document lists all control measures and isolation points to ensure the process is locked out (see Appendix 15.3.1). With the assistance of MII Mechanical Contractors, the existing VEGA (yellow in colour) instruments were removed from each vessel, following isolation of the 24V control loop via the CHARM supplies and the cables being removed from each device. The new Rosemount instruments were placed next to the VEGA existing guided wave radars to check the length of the probes, it was important that each new instrument was identical in length. 18TA0306LT20 Rosemount probe was slightly too long when compared to the existing instrument. MII Contractors took the probe back to their workshop to cut it to the required length.

Once installed, with new spiral wound gasket joints on the flanged connections, the Rosemount guided wave radar software, called Radar Master was used on the E/I laptop to communicate with each of the level instruments to go through the guided setup, where information such as the probe length, hold off distance, nozzle distance and upper and lower ranges were set. To determine these values the original VEGA setup values and tank dimension drawings were used. The appendices show the implementation stages (see Appendix 1.1). This software was then utilised to carry out the instrument proof tests and interlock testing (see Appendix 1.1).

# Testing / Evaluation / Analysis

Once installed, the manufacturer software, Rosemount Radar Master and a laptop were used to communicate with and setup each device, as shown in (see Appendices 15.3.4.1 and 15.3.5.1). The testing phase of this project involved proof testing, which is a test of the 4-20mA output of the device through the Delta V operating system and an interlock test to follow. The interlock test proves the safety actions that the device will initiate if a high level is detected. It was important to check the level reading against the existing BPCS level instrument to prove that the dimensions had been setup correctly.

As you can see in the interlock testing (see Appendix 15.4.1), containing a scanned copy of the first interlock test on 18TA0306 vessel, the instrument passed the 4-20mA proof tests and initiated all of the interlock actions at the correct level readings as expected. The proof tests involve simulating a 4-20mA signal from the instrument using the Rosemount radar software, this signal travels to the CHARM Smart SIS Logic Solver and through the Delta V operating system to the plant operator’s screen, where a percentage level is shown on a mimic. The voltage of the device is also checked at 4mA, it is expected that the voltage measured at the device to be above 20V and at 20mA, this should not drop by more than 5V. Next the trip actions are checked, this involves slowly increasing the mA output signal of the device until the trip value is reached, at this point the interlock actions should occur, this part of the test proves that the Delta V programming is correct. These interlock tests were carried out by Adam Cross, a trained Electrical and Instrumented Technician and the plant engineer. Further checks on the level reading were carried out (see Appendix 15.3.4.1), this included an echo curve analysis, to check if any unexpected signals were being detected between the device head and the liquid. It became apparent that the device was detecting the flanged pipe that it was mounted to, as the level reading was top scale (100%), to fix this problem, the tank dimension drawing was used so that the nozzle height could be set within the software, this tells the instrument to ignore anything within this region.

The same setup, proof testing and interlock testing was carried out on 18TA0307 vessel, (see Appendix 15.3.5.1) and (see Appendix 15.4.2). [14]

# Conclusion

The proof testing and interlock testing of these devices prove that they are installed and function correctly and that overall, this project was a success. The new level instruments now meet the required SIL2 specification and have therefore reduced the probability of failure on demand.

The final project costs were also massively under the £20,000 project budget, at £9,934.42 which is also £6145 under the initial estimate before contingency of £16,080. This is broken down into a saving of £3715 over the instrument cost estimate and a £2520 saving on engineering department estimated costs. This is mainly due to lack of experience in project planning and therefore vastly overestimating the amount of project time that was required but it was better to overestimate this than underestimate. Final costs are shown in the costings document (see Appendix 15.4.3).

The Gantt chart created at the start of the project (see Appendix 15.2.1), allocated deadlines that needed to be followed for the project to be a success. As you can see, some delays occurred and have been documented on the chart. These delays occurred due to unforeseen circumstances and had a knock-on effect throughout the project, this was documented in the logbook (see Appendix 1.1.1). My company had arranged at short notice to send me on two training courses throughout May and June where I was away for 2 weeks, this affected the project timing throughout, but I did my best to overcome these issues to get the project implemented prior to the deadline set.

The final implemented solution satisfies many, if not all of the requirements set out in the user requirement (see Appendix 15.2.6) and product design specification (see Appendix 15.2.7). The main, must have features set out in the user requirement document were met, the device uses 4-20mA HART Protocol and is therefore compatible with the Delta V operating system, it comes with its own manufacturer software to aid in setup and testing purposes, and the device provides all the required information to the user, such as liquid distance as well as liquid level. Another feature that the Rosemount 5301 has that was not essential but was nice to have, is a built in LCD screen to show all the instrument measuring information.

Both devices also satisfy the requirements set out in the PDS, they are guided wave radar type with an accuracy of +/- 2mm and have the required SIL2 certification to IEC 61508 as well as the ATEX certification to comply with the ATEX Directive 99/92/EC and Directive 2014/34/EU (see Appendix 15.2.8). They are IP66/67 rated making them ideal for the outdoor environment, the probes are made of 316L chemical resistant metal, and the transmitter housing is also made of metal for longevity. Due to meeting all the requirements set out in these documents and satisfying the aim and objectives of this project, I believe the project can be deemed an overall success.

As this project and all parts and components used are to a high standard, I am hopeful that there will be no issues to report with both level transmitters and I now have peace of mind after completing the testing phases, that if they are needed as a safety barrier at any point in the future, that they will operate to prevent a dangerous accident from occurring.

## Reflection

I very much enjoyed being a part of the projects department at my workplace while working on this project and really enjoyed learning more about SIL and SIS instrumentation concepts. The main thing that I have learnt throughout this project is the importance of time management and planning. I’ve learnt that it’s important to try to account for any unforeseen circumstances. I didn’t give myself any time within the Gantt chart planning to account for the work-related courses that I went on which therefore caused a lot of unnecessary stress to myself and delays to the project plan. In future I would look to overestimate the time it would take to do each task which would allow for some leeway over the course of the project.

I feel that the documents created during the research and planning stages, such as the feasibility studies and character selection matrixes were very beneficial and really helped to highlight the best solution for this project. This led to the project being a success as the device chosen satisfied all the design requirements.

Many invaluable skills and techniques have been gained throughout the process of this project that will definitely be applied to future projects.

# References

[1]	=Method, “TUV 61611 Function Safety Training,” 2022.

[2]	R. Fern Andez Blanco, “Understanding hazards, consequences, LOPA, SILs, PFD, and RRFs as related to risk and hazard assessment,” 2014, doi: 10.1002/prs.11700.

[3]	“Level Instruments Design Rules | Level Measurement Design Guide.” https://instrumentationtools.com/level-instruments-design-rules/ (accessed Jul. 02, 2022).

[4]	“About Guided Wave Radar | Emerson GB.” https://www.emerson.com/en-gb/automation/measurement-instrumentation/level/continuous-level-measurement/about-guided-wave-radar (accessed Jun. 28, 2022).

[5]	“Functional safety - Electrical, Control and Instrumentation (E, C&I) - HSE.” https://www.hse.gov.uk/eci/functional.htm (accessed May 01, 2022).

[6]	“DeltaV SIS TM Process Safety System”, Accessed: May 01, 2022. [Online]. Available: https://www.emerson.com/documents/automation/brochure-deltav-sis-system-overview-deltav-sis-en-56616.pdf

[7]	D. SIS - Emerson, “DeltaV SIS TM HART Capabilities,” 2020, Accessed: May 01, 2022. [Online]. Available: www.emerson.com/deltavsis

[8]	“DeltaV SIS TM Process Safety System”, Accessed: May 01, 2022. [Online]. Available: https://www.emerson.com/documents/automation/brochure-deltav-sis-system-overview-deltav-sis-en-56616.pdf

[9]	D. SIS - Emerson, “Product Data Sheet DeltaV SIS Process Safety System DeltaV Safety Instrumented System (SIS) TM with Electronic Marshalling,” 2021, Accessed: May 01, 2022. [Online]. Available: www.emerson.com/deltavsis

[10]	“ATEX and explosive atmospheres - Fire and explosion.” https://www.hse.gov.uk/fireandexplosion/atex.htm (accessed Jul. 02, 2022).

[11]	“Continuous Level Measurement: TDR/GWR Sensor for Liquids: VEGAFLEX 81 | VEGA | VEGA.” https://www.vega.com/en-uk/products/product-catalog/level/guided-wave-radar/vegaflex-81 (accessed Jun. 30, 2022).

[12]	“Rosemount 5300 Level Transmitter - Guided Wave Radar | Emerson GB.” https://www.emerson.com/en-gb/catalog/automation/measurement-instrumentation/tank-gauging/rosemount-sku-5300-gwr-transmitter-en-gb?fetchFacets=true#facet:&partsFacet:&facetLimit:&productBeginIndex:0&partsBeginIndex:0&orderBy:&partsOrderBy:&pageView:list&minPrice:&maxPrice:&pageSize:&facetRange:& (accessed Jun. 30, 2022).

[13]	“Guided Radar / Time-of-Flight - Levelflex FMP51 | Endress+Hauser.” https://www.uk.endress.com/en/field-instruments-overview/level-measurement/Guided-Radar-Levelflex-FMP51?g.filters=%7B%22endress%3Abusiness-area%22%3A%5B%22level%22%5D%2C%22endress%3Ameasuring-principle-parameter%22%3A%5B%22guided-wave-radar%22%5D%7D&t.tabId=product-overview (accessed Jun. 30, 2022).

[14]	S. Nunns and C. Eng, “HSE Health & Safety Executive Principles for proof testing of safety instrumented systems in the chemical industry,” 2002, Accessed: May 01, 2022. [Online]. Available: http://www.hse-databases.co.uk

[15]	R. - Emerson, “Manual: Rosemount 5300:SIS Level Transmitter; Manual: Rosemount 5300:SIS Level Transmitter”, Accessed: Jul. 06, 2022. [Online]. Available: https://www.emerson.com/documents/automation/manual-rosemount-5300-sis-level-transmitter-en-7227814.pdf

# Appendices

## Research

### Relevant Standards

### Level Instrument Quotations

#### Endress+Hauser

#### Emerson Rosemount

#### VEGA

### Level Instrument Character Selection Matrix

## Planning

### Gantt Chart

### Feasibility Studies

### Cost and Time Estimates

#### Information

#### Instrumentation

#### Engineering

#### Total Cost Estimate

### Tank Dimension Drawings

### Resources

### User Requirement Specification

### Product Design Specification

### Certificates for Installed Instruments

#### 18TA0306

#### 18TA0307

### Data Sheet

Due to the Rosemount 5300 Series SIS Transmitter manual being 40+ pages, please refer to reference [15]

## Implementation

### Permit to Work

### CHARM Panel

### Instruments

### 18TA0306LT20

#### Rosemount Radar Master Device Setup

### 18TA0307LT20

#### Rosemount Radar Master Device Setup

### Instrument loop drawing

## Testing & Reflection

### Interlock Testing 18TA0306

### Interlock Testing 18TA0307

### Final Costs

#### Information

#### Instrumentation

#### Engineering

#### Total Cost

### Logbook