Environmental Management System
Site Audit Report 


	Department/ College/ Site being audited: 
Dynefor
	Date of audit: 
02/10/2025

	Auditee: 
University of Wales Trinity St David
	Auditor:
Robert Saunders



	Objectives 
· To assess the implementation of the EMS at each site


	Summary
Auditor recommends immediate action for major non-conformance identified regarding the use of AFFF fire extinguishers. 4 Minor non-conformities identified. Paper work provided and PPM seen to be inline with legislative requirements.

	
Air Conditioning
Air conditioning service report sampled:
09/04/2025
All A/C systems
No faults to report

Auditor confirms frequency of check in line with refrigerant charge via:
WCC 9a + 9b – R410a, 27.35 Kg charge
57.11 TCO2e Eq
Leak check performed 6 monthly

Waste Management 
Hazardous Waste Consignment note
LAS – CBDU5499
Fluorescent Tubes – 200121
11/09/2024
All parts Complete

Hazardous Waste Consignment Note
LAS – CBDU5499
Aerosol Cans – 150111
12/12/2024
All Parts Complete

Plant Protection Products 
No Plant protection products used on site

Boilers
Boiler servicing sampled
Dynevor Campus
Ceramics building
13/03/2025

Dynevor Campus
Ceramics building
12/03/2025

Energy Performance of Buildings
DECs witnessed.
Observation: DEC provided out of date for time of audit – Dated 31/09/2025
TM44 sampled
Valid until 26th February

Onsite Controls - Walk round
Waste segregation seen to be in line with legislative requirements.
Minor: Fluorescent tubes stored loose outside of external waste storage area, Aerosols mixed with metal resin containers.
COSHH cupboard seen to be appropriate, with lipped containment.
Spill kits present at required locations.
Sediment traps present in plaster and ceramics workshops. Silt buster in main sink with bag also used in sink to catch larger siltage.
Waste dye hazardous bin present in dye room.
Minor: Acid cabinet in dye room seen to be metal, advisable plastic cabinet due to reduced reactivity, no acid spill kit present.
Major: Fire extinguishers seen to be serviced from 2012, AFFF foam likely containing PFOS chemicals which are now banned from use.
Minor: Waste stored within COSHH cabinets (white spirits containers).
Minor: Powder extinguisher present in photography chemical store, dated 1986.


	Observations raised

	No.
	Description 

	1.
	Observation: DEC provided out of date for time of audit – Dated 31/09/2025


	2. 
	

	3.
	

	4.
	

	Non- conformance raised 

	No. 
	Minor/ Major  
	Description 

	1.
	Minor
	Fluorescent tubes stored loose outside of external waste storage area, Aerosols mixed with metal resin containers.

	2.
	Minor
	Acid cabinet in dye room seen to be metal, advisable plastic cabinet due to reduced reactivity, no acid spill kit present.

	3.
	Major
	Fire extinguishers seen to be serviced from 2012, AFFF foam likely containing PFOS chemicals which are now banned from use.

	4.
	Minor
	Waste stored within COSHH cabinets (white spirits containers).

	5.
	Minor
	Powder extinguisher present in photography chemical store, dated 1986.



	Terms 

	Term 
	Description 

	Observation 
	Identifies an issue that requires attention to improve the operation of the EMS
and that if left un-addressed is likely to lead to a non-conformance during future audits, an example of good environmental practise that deserves recognition or a flag for re-visit at the next audit.

	Minor Non- conformance  
	Areas where the EMS is deviating from the Green Dragon Standard requirements in a minor or technical way.

	Major Non- conformance 
	Serious deviation from the Green Dragon Standard requirements, e.g. legal non-compliance. 



